## config
| Property | Value
0 | BaseMVA | 100.0
1 | Version | 5
2 | Name
3 | Comments
4 | ModelVersion | 5
5 | UserName | 123870405492120:POSMARFE
6 | program | GridCal

## modelling_authority
idtag | name | code | action | comment

## area
| idtag | name | code | action | comment | longitude | latitude | color
0 | ed93a2fb68c64d0c95e44e90d03f1a55 | Default area |  | No action |  | 0.0 | 0.0 | #4b7d22

## zone
| idtag | name | code | action | comment | longitude | latitude | color | area
0 | f0e88cfdfedc4453a04cfff7aa606feb | Default zone |  | No action |  | 0 | 0 | #793876

## country
| idtag | name | code | action | comment | longitude | latitude | color
0 | 6b0d084937be4b69ac8d4e5b8b2d03bf | Default country |  | No action |  | 0.0 | 0.0 | #0c4e12

## community
idtag | name | code | action | comment | longitude | latitude | color | country

## region
idtag | name | code | action | comment | longitude | latitude | color | community

## municipality
idtag | name | code | action | comment | longitude | latitude | color | region

## substation
| idtag | name | code | action | comment | longitude | latitude | color | area | zone | country | community | region | municipality | modelling_authority | address | irradiation | temperature | wind_speed | terrain_roughness
0 | d7fd45daa58e4484bf78c855c860b8aa | Default substation |  | No action |  | 0 | 0 | #3d7d95 | [8 empty] | 0 | 0 | 0 | 0.2

## voltage_level
idtag | name | code | action | comment | modelling_authority | Vnom | substation

## technology
| idtag | name | code | action | comment | name2 | name3 | name4 | color
0 | 204533bc736c4b2ca2a092038eb67fbe | 5da86cd98d444c6dbf95f4e4089451ff |  | No action |  |  |  |  | #1a0a73

## fuel
idtag | name | code | action | comment | cost | color

## emission
idtag | name | code | action | comment | cost | color

## facility
idtag | name | code | action | comment | longitude | latitude | color

## bus
| idtag | name | code | action | comment | modelling_authority | active | is_slack | is_dc | internal | Vnom | Vm0 | Va0 | Vmin | Vmax | Vm_cost | angle_min | angle_max | angle_cost | r_fault | x_fault | x | y | h | w | country | area | zone | substation | voltage_level | longitude | latitude | ph_a | ph_b | ph_c | ph_n | is_grounded
0 | 131557160c40462f9db94a50151714c3 | Bus 0 |  | No action |  |  | TRUE | FALSE | FALSE | FALSE | 10 | 1 | 0 | 0.9 | 1.1 | 1 | -6.28 | 6.28 | 0 | 0 | 0 | 494 | -436 | 14 | 180 | 6b0d084937be4b69ac8d4e5b8b2d03bf | ed93a2fb68c64d0c95e44e90d03f1a55 | f0e88cfdfedc4453a04cfff7aa606feb | d7fd45daa58e4484bf78c855c860b8aa |  | 0 | 0 | TRUE | TRUE | TRUE | TRUE | TRUE
1 | 1df58650151f42bb95a1fd1a375eee68 | Bus 1 |  | No action |  |  | TRUE | FALSE | FALSE | FALSE | 10 | 1 | 0 | 0.9 | 1.1 | 1 | -6.28 | 6.28 | 0 | 0 | 0 | 37 | 0 | 14 | 180 | 6b0d084937be4b69ac8d4e5b8b2d03bf | ed93a2fb68c64d0c95e44e90d03f1a55 | f0e88cfdfedc4453a04cfff7aa606feb | d7fd45daa58e4484bf78c855c860b8aa |  | 0 | 0 | TRUE | TRUE | TRUE | TRUE | TRUE
2 | f9070e585ad14dc893b7b7680905459b | Bus 2 |  | No action |  |  | TRUE | FALSE | FALSE | FALSE | 10 | 1 | 0 | 0.9 | 1.1 | 1 | -6.28 | 6.28 | 0 | 0 | 0 | 953 | -1 | 14 | 180 | 6b0d084937be4b69ac8d4e5b8b2d03bf | ed93a2fb68c64d0c95e44e90d03f1a55 | f0e88cfdfedc4453a04cfff7aa606feb | d7fd45daa58e4484bf78c855c860b8aa |  | 0 | 0 | TRUE | TRUE | TRUE | TRUE | TRUE
3 | 1cab1351b5d74c889a0212d3cdc0f341 | Bus 3 |  | No action |  |  | TRUE | FALSE | FALSE | FALSE | 10 | 1 | 0 | 0.9 | 1.1 | 1 | -6.28 | 6.28 | 0 | 0 | 0 | 17 | -713 | 14 | 180 | 6b0d084937be4b69ac8d4e5b8b2d03bf | ed93a2fb68c64d0c95e44e90d03f1a55 | f0e88cfdfedc4453a04cfff7aa606feb | d7fd45daa58e4484bf78c855c860b8aa |  | 0 | 0 | TRUE | TRUE | TRUE | TRUE | TRUE
4 | 7563a5cdfc2843fbb2e2096a8f7a6a2d | Bus 4 |  | No action |  |  | TRUE | TRUE | FALSE | FALSE | 10 | 1 | 0 | 0.9 | 1.1 | 1 | -6.28 | 6.28 | 0 | 0 | 0 | 0 | -428 | 14 | 180 | 6b0d084937be4b69ac8d4e5b8b2d03bf | ed93a2fb68c64d0c95e44e90d03f1a55 | f0e88cfdfedc4453a04cfff7aa606feb | d7fd45daa58e4484bf78c855c860b8aa |  | 0 | 0 | TRUE | TRUE | TRUE | TRUE | TRUE

## bus_bar
idtag | name | code | action | comment | modelling_authority | voltage_level | cn

## connectivity node
idtag | name | code | action | comment | modelling_authority | Vnom | dc | internal | bus | voltage_level

## load
| idtag | name | code | action | comment | modelling_authority | bus | cn | active | mttf | mttr | capex | opex | build_status | Cost | facility | technologies | scalable | use_kw | P | Q | Ir | Ii | G | B
0 | f512c5ab0f634b968e73a69ad6e7683a | Load@Bus 0 |  | No action |  |  | 131557160c40462f9db94a50151714c3 |  | TRUE | 0 | 0 | 0 | 0 | Commissioned | 1200 |  | {} | TRUE | FALSE | 18 | 0 | 0 | 0 | 0 | 0

## static_generator
idtag | name | code | action | comment | modelling_authority | bus | cn | active | mttf | mttr | capex | opex | build_status | Cost | facility | technologies | scalable | use_kw | P | Q

## battery
idtag | name | code | action | comment | modelling_authority | bus | cn | active | mttf | mttr | capex | opex | build_status | Cost | facility | technologies | scalable | use_kw | control_bus | control_cn | P | Pmin | Pmax | srap_enabled | is_controlled | Pf | Vset | Snom | Qmin | Qmax | use_reactive_power_curve | q_curve | R1 | X1 | R0 | X0 | R2 | X2 | Cost2 | Cost0 | StartupCost | ShutdownCost | MinTimeUp | MinTimeDown | RampUp | RampDown | enabled_dispatch | emissions | fuels | Enom | max_soc | min_soc | soc_0 | charge_efficiency | discharge_efficiency | discharge_per_cycle

## generator
| idtag | name | code | action | comment | modelling_authority | bus | cn | active | mttf | mttr | capex | opex | build_status | Cost | facility | technologies | scalable | use_kw | control_bus | control_cn | P | Pmin | Pmax | srap_enabled | is_controlled | Pf | Vset | Snom | Qmin | Qmax | use_reactive_power_curve | q_curve | R1 | X1 | R0 | X0 | R2 | X2 | Cost2 | Cost0 | StartupCost | ShutdownCost | MinTimeUp | MinTimeDown | RampUp | RampDown | enabled_dispatch | emissions | fuels
0 | 8b44631c87d74930945dae21e14f3765 | gen |  | No action |  |  | 1df58650151f42bb95a1fd1a375eee68 |  | TRUE | 0 | 0 | 0 | 0 | Commissioned | 1 |  | {'204533bc736c4b2ca2a092038eb67fbe': <GridCalEngine.Devices.Associations.association.Association object at 0x0000028EC38B3B30>} | TRUE | FALSE |  |  | 6 | 0 | 9999 | TRUE | TRUE | 0.8 | 1 | 9999 | -9999 | 9999 | FALSE | [[0.0, -9999.0, 9999.0]] | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 0 | 0 | 0 | 0 | 0 | 0 | 1e+20 | 1e+20 | TRUE | {} | {}
1 | b88cdfe159a44a60affbb5aee8e8f54c | gen |  | No action |  |  | f9070e585ad14dc893b7b7680905459b |  | TRUE | 0 | 0 | 0 | 0 | Commissioned | 1 |  | {'204533bc736c4b2ca2a092038eb67fbe': <GridCalEngine.Devices.Associations.association.Association object at 0x0000028EC38B2C00>} | TRUE | FALSE |  |  | 7 | 0 | 9999 | TRUE | TRUE | 0.8 | 1 | 9999 | -9999 | 9999 | FALSE | [[0.0, -9999.0, 9999.0]] | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 0 | 0 | 0 | 0 | 0 | 0 | 1e+20 | 1e+20 | TRUE | {} | {}
2 | 48f51fb0e2b84437b1ab2b8b2c807512 | gen |  | No action |  |  | 1cab1351b5d74c889a0212d3cdc0f341 |  | TRUE | 0 | 0 | 0 | 0 | Commissioned | 1 |  | {'204533bc736c4b2ca2a092038eb67fbe': <GridCalEngine.Devices.Associations.association.Association object at 0x0000028EC38B12E0>} | TRUE | FALSE |  |  | 5 | 0 | 9999 | TRUE | TRUE | 0.8 | 1 | 9999 | -9999 | 9999 | FALSE | [[0.0, -9999.0, 9999.0]] | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 0 | 0 | 0 | 0 | 0 | 0 | 1e+20 | 1e+20 | TRUE | {} | {}

## shunt
idtag | name | code | action | comment | modelling_authority | bus | cn | active | mttf | mttr | capex | opex | build_status | Cost | facility | technologies | scalable | use_kw | G | B | G0 | B0

## linear_shunt
idtag | name | code | action | comment | modelling_authority | bus | cn | active | mttf | mttr | capex | opex | build_status | Cost | facility | technologies | scalable | use_kw | G | B | G0 | B0 | is_nonlinear | g_steps | b_steps | Gmax | Gmin | Bmax | Bmin | active_steps | step | Vset

## external_grid
idtag | name | code | action | comment | modelling_authority | bus | cn | active | mttf | mttr | capex | opex | build_status | Cost | facility | technologies | scalable | use_kw | P | Q | mode | substituted_device_id | Vm | Va

## current_injection
idtag | name | code | action | comment | modelling_authority | bus | cn | active | mttf | mttr | capex | opex | build_status | Cost | facility | technologies | scalable | use_kw | Ir | Ii

## wires
| idtag | name | code | action | comment | R | X | GMR | max_current | stranding | material | diameter
0 | 411960af624848df99399fafa757c998 | -_ACSR_0.902 |  | No action |  | 0.857492256 | 0.0 | 0.001274 | 0.177 |  |  | 0.0
1 | 8e25856b7cdd4c94b3da871f9a173e0c | 7 STRD_Copper_0.833 |  | No action |  | 0.475348968 | 0.0 | 0.003024 | 0.18 |  |  | 0.0
2 | 8186c23b6cff4b2dbdda9059db0ee529 | CLASS A_AA_0.833 |  | No action |  | 0.7605583488 | 0.0 | 0.003021 | 0.23 |  |  | 0.0
3 | 0be1666aadbb44df8834fc64821aca25 | 6/1_ACSR_0.803 |  | No action |  | 1.050117328 | 0.0 | 0.001274 | 0.18 |  |  | 0.0
4 | ed6065823a644e53a747b7f902e195c6 | 7 STRD_Copper_0.742 |  | No action |  | 0.5990018368 | 0.0 | 0.002691 | 0.22 |  |  | 0.0
5 | 935c35f22b7a4b1f915705d0ed9ff1a7 | 7/1_ACSR_0.826 |  | No action |  | 1.02526248 | 0.0 | 0.001536 | 0.156 |  |  | 0.0
6 | e0ab0b13a3e64bba8933c1b7637700e0 | AWG SLD_Copper_0.655 |  | No action |  | 0.587195784 | 0.0 | 0.002548 | 0.16 |  |  | 0.0
7 | d105b68bb23c407e8793ea5787d2efdc | CLASS A_AA_0.742 |  | No action |  | 0.9575330192 | 0.0 | 0.002691 | 0.19 |  |  | 0.0
8 | 166a7ffb29ca4b41956fcfe2bd0b41d0 | 6/1_ACSR_0.714 |  | No action |  | 1.286238384 | 0.0 | 0.001311 | 0.14 |  |  | 0.0
9 | 1d921544bb91456397460f0f0999a110 | AWG SLD_Copper_0.582 |  | No action |  | 0.7406744704 | 0.0 | 0.002271 | 0.14 |  |  | 0.0
10 | ffa4727eb12a41bfa4adae67674ec229 | 6/1_ACSR_0.635 |  | No action |  | 1.596923984 | 0.0 | 0.001332 | 0.17 |  |  | 0.0
11 | b31abb3a11264643a54483b8c17f2fbc | 7/1_ACSR_0.653 |  | No action |  | 1.58449656 | 0.0 | 0.001378 | 0.09 |  |  | 0.0
12 | f0ddbc92c3a54ca494f1ab62fbb23470 | AWG SLD_Copper_0.518 |  | No action |  | 0.9339209136 | 0.0 | 0.002021 | 0.12 |  |  | 0.0
13 | d701b81e9a564c87844297e525f71db0 | CLASS A_AA_0.589 |  | No action |  | 1.5242235536 | 0.0 | 0.002134 | 0.14 |  |  | 0.0
14 | de9ccf76d7a64211a92cdfc18bb7874a | 6/1_ACSR_0.566 |  | No action |  | 1.975960416 | 0.0 | 0.001268 | 0.1 |  |  | 0.0
15 | 63d1a17c1f5a4d979d7e52a55bcc5a2a | AWG SLD_Copper_0.462 |  | No action |  | 1.177498424 | 0.0 | 0.001798 | 0.12 |  |  | 0.0
16 | 1d2dfb7edc504c11b04140de0798c5b8 | 6/1_ACSR_0.503 |  | No action |  | 2.473057376 | 0.0 | 0.001201 | 0.065 |  |  | 0.0
17 | 1f31d194374b42a4ba2125e314e23649 | AWG SLD_Copper_0.411 |  | No action |  | 1.485077168 | 0.0 | 0.001603 | 0.11 |  |  | 0.0
18 | c73880485b464bb4a1f4f5845b183516 | CLASS A_AA_0.467 |  | No action |  | 2.4252117936 | 0.0 | 0.001692 | 0.09 |  |  | 0.0
19 | 9767f8f687cf4ecdaa15aef79716c76a | AWG SLD_Copper_0.367 |  | No action |  | 1.870327312 | 0.0 | 0.001426 | 0.08 |  |  | 0.0
20 | ee12861236e546abb94ad6cc38c22e06 | AWG SLD_Copper_0.326 |  | No action |  | 2.36121056 | 0.0 | 0.001268 | 0.075 |  |  | 0.0
21 | 196a5c5b82b5406787c037d2e9389019 | AWG SLD_Copper_0.291 |  | No action |  | 2.90540745696 | 0.0 | 0.001131 | 0.04 |  |  | 0.0
22 | 9991ef21775745e8996c2be5e16c4dce | AWG SLD_Copper_0.259 |  | No action |  | 3.66770564512 | 0.0 | 0.001006 | 0.02 |  |  | 0.0
23 | a065f6b1844c4597bcdbb358cca550d2 | AWG SLD_Copper_0.205 |  | No action |  | 5.82516858864 | 0.0 | 0.000799 | 0.01 |  |  | 0.0
24 | 6030607cef5b4eef8185db4613a7b05c | AWG SLD_Copper_0.163 |  | No action |  | 9.24115676064 | 0.0 | 0.000634 | 0.005 |  |  | 0.0
25 | 932ed653d6dd4eb78747a43ae6126cc2 | AWG SLD_Copper_0.129 |  | No action |  | 14.74277736544 | 0.0 | 0.0005 | 0.004 |  |  | 0.0
26 | 8af8ed6e43a04f938271c97a2a475696 | AWG SLD_Copper_0.102 |  | No action |  | 23.40866866912 | 0.0 | 0.000396 | 0.003 |  |  | 0.0
27 | 3fc232445d2c4813aa557d0c4314d49c | AWG SLD_Copper_0.091 |  | No action |  | 29.52153212336 | 0.0 | 0.000354 | 0.002 |  |  | 0.0
28 | 1e2ac7d9eabb47658d87e5c5407c6cc3 | AWG SLD_Copper_0.081 |  | No action |  | 37.0859187008 | 0.0 | 0.000314 | 0.001 |  |  | 0.0
29 | d1d9507b080242f88dbd2e8216f8a485 | AWG SLD_Copper_0.064 |  | No action |  | 59.3306969752 | 0.0 | 0.00025 | 0.23 |  |  | 0.0
30 | 3c1735b4cf6943c7a02b173e4056e629 | AWG SLD_Copper_0.051 |  | No action |  | 94.2098158592 | 0.0 | 0.000198 | 0.31 |  |  | 0.0
31 | 49ea09690bfc4cd6b0eba0937093634b | -_ACSR_1.011 |  | No action |  | 0.695935744 | 0.0 | 0.001359 | 0.202 |  |  | 0.0
32 | b9f043f6ff71454a91fa75334bf4d698 | 7 STRD_Copper_0.935 |  | No action |  | 0.3771723184 | 0.0 | 0.003392 | 0.27 |  |  | 0.0
33 | afac074978bf4a1abc46f924da4ff117 | CLASS A_AA_0.935 |  | No action |  | 0.602730064 | 0.0 | 0.003383 | 0.36 |  |  | 0.0
34 | ad76f5f722974199b28df7172b4deaeb | -_ACSR_1.135 |  | No action |  | 0.556127224 | 0.0 | 0.001554 | 0.23 |  |  | 0.0
35 | e4b2ddafe38b47c0bf3f4407b704350f | 7 STRD_Copper_1.052 |  | No action |  | 0.2988795472 | 0.0 | 0.003816 | 0.42 |  |  | 0.0
36 | 207d2b243e9c470e9c01eee2613703d7 | CLASS A_AA_1.052 |  | No action |  | 0.4778344528 | 0.0 | 0.00381 | 0.3 |  |  | 0.0
37 | f9c7ca4246214272b192c0b107b19086 | 12 STRD_Copper_1.25 |  | No action |  | 0.2373637984 | 0.0 | 0.004752 | 0.42 |  |  | 0.0
38 | 4e58ba51161f400f8ec42cf1a5d95f13 | 6/1_ACSR_1.275 |  | No action |  | 0.4492513776 | 0.0 | 0.001829 | 0.263 |  |  | 0.0
39 | 4b029381e42142bea3c5ee0cfef2a036 | 7 STRD_Copper_1.179 |  | No action |  | 0.2373637984 | 0.0 | 0.004279 | 0.15 |  |  | 0.0
40 | 681bb08bf4e74e19a6b0d55e2aa4fe20 | CLASS A_AA_1.179 |  | No action |  | 0.3796578032 | 0.0 | 0.004267 | 0.49 |  |  | 0.0
41 | 5c5f4e4930964dac973b2d4604ebac08 | INCH STE_Steel_0.953 |  | No action |  | 2.67189616 | 0.0 | 3e-06 | 0.48 |  |  | 0.0
42 | b38c4a4533d540caa0c2c8a4d2cd4b52 | 12 STRD_Copper_1.402 |  | No action |  | 0.1882754736 | 0.0 | 0.005334 | 0.34 |  |  | 0.0
43 | 27e5e12128234e6bb8d077cf84162ccc | 19 STRD_Copper_1.341 |  | No action |  | 0.1882754736 | 0.0 | 0.005084 | 0.48 |  |  | 0.0
44 | ae5dde8d592d47a98e58829ded1852d0 | 6/1_ACSR_1.43 |  | No action |  | 0.3678517504 | 0.0 | 0.002481 | 0.299 |  |  | 0.0
45 | 5e6822f3912d479a95a2bd9b97970994 | 7 STRD_Copper_1.326 |  | No action |  | 0.1882754736 | 0.0 | 0.004813 | 0.54 |  |  | 0.0
46 | 36d71c6fae2c4ce68c50bccac885f778 | CLASS A_AA_1.326 |  | No action |  | 0.3007436608 | 0.0 | 0.004816 | 0.54 |  |  | 0.0
47 | f8cc9657a5c44d32a91e15c4aaef66c8 | 12 STRD_Copper_1.524 |  | No action |  | 0.1596923984 | 0.0 | 0.005797 | 0.329 |  |  | 0.0
48 | 2668971ee339471ea044d9303a2dd046 | 19 STRD_Copper_1.458 |  | No action |  | 0.1596923984 | 0.0 | 0.005526 | 0.46 |  |  | 0.0
49 | 8229f9282b694243927b76bfff9cf0a3 | CON LAY_AA_1.44 |  | No action |  | 0.254762192 | 0.0 | 0.005212 | 0.32 |  |  | 0.0
50 | 9dd1468267a44c2a8dfb8a246fe62262 | 26/7_ACSR_1.631 |  | No action |  | 0.239227912 | 0.0 | 0.006614 | 0.61 |  |  | 0.0
51 | 33c6b202feed4d9cbe2e0599784ed91a | CLASS A_AA_1.488 |  | No action |  | 0.2386065408 | 0.0 | 0.005395 | 0.61 |  |  | 0.0
52 | 780dd9bf49324ecaaee94439c21979b0 | 12 STRD_Copper_1.669 |  | No action |  | 0.133594808 | 0.0 | 0.00634 | 0.49 |  |  | 0.0
53 | b0a72302d4cc4b138b7354fc480dc0b0 | 19 STRD_Copper_1.598 |  | No action |  | 0.133594808 | 0.0 | 0.006056 | 0.5 |  |  | 0.0
54 | 6c024e1f2bd9427180ee90ff0d643c8c | 26/7_ACSR_1.727 |  | No action |  | 0.2125089504 | 0.0 | 0.00701 | 0.35 |  |  | 0.0
55 | 34973b92e3634d2489c5bd61e9cc6d88 | 30/7_ACSR_1.778 |  | No action |  | 0.2125089504 | 0.0 | 0.007346 | 0.53 |  |  | 0.0
56 | 4c776cf704b0426fa482e513fd4330ff | CON LAY_AA_1.598 |  | No action |  | 0.2125089504 | 0.0 | 0.006035 | 0.53 |  |  | 0.0
57 | 16072e27a9ca4896ac362d0306b01268 | 26/7_ACSR_1.831 |  | No action |  | 0.1901395872 | 0.0 | 0.007437 | 0.41 |  |  | 0.0
58 | c39a068e42944ee1b1a51c1ac6217ee6 | 30/7_ACSR_1.882 |  | No action |  | 0.1901395872 | 0.0 | 0.007772 | 0.67 |  |  | 0.0
59 | f803b8ae257e438da98f6f45df6647b6 | CLASS A_AA_1.692 |  | No action |  | 0.189518216 | 0.0 | 0.006401 | 0.67 |  |  | 0.0
60 | 19b6c5ecd9794378a1cd76c7abe90c2f | 12 STRD_Copper_1.803 |  | No action |  | 0.1146429864 | 0.0 | 0.006858 | 0.399 |  |  | 0.0
61 | 64b507b1ed56404cb7b59df5e87853af | 19 STRD_Copper_1.725 |  | No action |  | 0.1146429864 | 0.0 | 0.006523 | 0.59 |  |  | 0.0
62 | baf17aa26ded401886789c5e04f2d1d1 | CON LAY_AA_1.725 |  | No action |  | 0.1826831328 | 0.0 | 0.006523 | 0.6 |  |  | 0.0
63 | c20c08b486074d429249b45d63b81570 | 26/7_ACSR_1.989 |  | No action |  | 0.1609351408 | 0.0 | 0.008077 | 0.44 |  |  | 0.0
64 | e045cc6acda14529857705c1e5baeddf | 30/7_ACSR_2.047 |  | No action |  | 0.1609351408 | 0.0 | 0.008473 | 0.73 |  |  | 0.0
65 | a1609da285664d22bdc40ec897c868bf | CLASS A_AA_1.839 |  | No action |  | 0.1603137696 | 0.0 | 0.006949 | 0.78 |  |  | 0.0
66 | 947a5afb349543c6a89adce78ed0a56d | 19 STRD_Copper_1.844 |  | No action |  | 0.10059999728 | 0.0 | 0.00698 | 0.45 |  |  | 0.0
67 | 04ae7569500a4737a1dc438510cc07a9 | 19 STRD_Copper_1.956 |  | No action |  | 0.08966386416 | 0.0 | 0.007407 | 0.67 |  |  | 0.0
68 | 14f5525192b7408d94fefdea36a54ad6 | CON LAG_AA_1.956 |  | No action |  | 0.1422940048 | 0.0 | 0.007407 | 0.67 |  |  | 0.0
69 | 095044bd4a524dff9988f1d8aeb2d650 | 26/7_ACSR_2.179 |  | No action |  | 0.1342161792 | 0.0 | 0.008839 | 0.51 |  |  | 0.0
70 | f142a7d75192459f83244e00e90725fd | 30/7_ACSR_2.243 |  | No action |  | 0.1342161792 | 0.0 | 0.009266 | 0.84 |  |  | 0.0
71 | 93e27ede1dd443e4ba94044798f377c8 | CLASS A_AA_2.019 |  | No action |  | 0.1342161792 | 0.0 | 0.007742 | 0.84 |  |  | 0.0
72 | 3dc2799cbcd5460b9be9ae69a12003da | 19 STRD_Copper_2.06 |  | No action |  | 0.08096466736 | 0.0 | 0.007803 | 0.483 |  |  | 0.0
73 | a984a443c5f84b33aa6f7d2218e3193e | 37 STRD_Copper_2.068 |  | No action |  | 0.08096466736 | 0.0 | 0.007925 | 0.73 |  |  | 0.0
74 | 67f7ef9d54ed4337bccf32e6d8412ea8 | CON LAY_AA_2.065 |  | No action |  | 0.1280024672 | 0.0 | 0.007925 | 0.73 |  |  | 0.0
75 | 607edfb554ae4434938a1fd00491eda8 | 26/7_ACSR_2.355 |  | No action |  | 0.11551290608 | 0.0 | 0.00954 | 0.56 |  |  | 0.0
76 | 3b72a5317b764724841f26dc23e2f778 | 30/7_ACSR_2.421 |  | No action |  | 0.11551290608 | 0.0 | 0.009997 | 0.94 |  |  | 0.0
77 | 0c17a4e292a74ecfb7ea919197ab2b8a | CLASS A_AA_2.179 |  | No action |  | 0.1155750432 | 0.0 | 0.008382 | 0.52 |  |  | 0.0
78 | bd79e54888c54d77843c2278dbabf61e | 37 STRD_Copper_2.263 |  | No action |  | 0.0680401464 | 0.0 | 0.008687 | 0.76 |  |  | 0.0
79 | d67cbbd8ea1c4c0eab4f5b12862e410a | CON LAY_AA_2.263 |  | No action |  | 0.1068758464 | 0.0 | 0.008687 | 0.75 |  |  | 0.0
80 | 200d85badacd48e780a75d0daad46e48 | 26/7_ACSR_2.454 |  | No action |  | 0.1068758464 | 0.0 | 0.009967 | 0.78 |  |  | 0.0
81 | d27965bff0c14091b37297cf62095366 | 54/7_ACSR_2.421 |  | No action |  | 0.110293388 | 0.0 | 0.009784 | 0.78 |  |  | 0.0
82 | 8a93af94f6ba46ff883d140acc0ccaa3 | 27/7_ACSR_2.515 |  | No action |  | 0.10053786016 | 0.0 | 0.010211 | 0.77 |  |  | 0.0
83 | 09cb7b6d06ae41889f1e4a20e0ab530f | 30/19_ACSR_2.588 |  | No action |  | 0.10053786016 | 0.0 | 0.010698 | 0.62 |  |  | 0.0
84 | 98df820d1bf649049b04f41fc0db83a9 | 54/7_ACSR_2.482 |  | No action |  | 0.10488745856 | 0.0 | 0.010028 | 0.8 |  |  | 0.0
85 | ab6a79ed0512433ca3cec7341686b4f8 | CLASS A_AA_2.332 |  | No action |  | 0.1012835056 | 0.0 | 0.008961 | 1.04 |  |  | 0.0
86 | 0d7316b4ef6d4b8ea5118a895c0c9a7d | 54/7_ACSR_2.54 |  | No action |  | 0.09948152912 | 0.0 | 0.010272 | 0.58 |  |  | 0.0
87 | 9772d32b48b148ea93ed865e5653785d | 37 STRD_Copper_2.446 |  | No action |  | 0.05884385264 | 0.0 | 0.009388 | 0.84 |  |  | 0.0
88 | b7e560871af14fdba4598da56a870a62 | CON LAY_AA_2.446 |  | No action |  | 0.0919629376 | 0.0 | 0.009388 | 0.84 |  |  | 0.0
89 | b3bfc8e408264702a398c4c4e7155d0d | 26/7_ACSR_2.67 |  | No action |  | 0.08960172704 | 0.0 | 0.01082 | 0.83 |  |  | 0.0
90 | a04f5a519016418d86a1de45d8d3194e | 30/19_ACSR_2.746 |  | No action |  | 0.08960172704 | 0.0 | 0.011339 | 0.68 |  |  | 0.0
91 | b93e22eb76a1424ab0c53724c19cd249 | 54/7_ACSR_2.631 |  | No action |  | 0.09208721184 | 0.0 | 0.010638 | 1.09 |  |  | 0.0
92 | 95a725d24e9f471e86d1f6af01edb6a0 | CLASS A_AA_2.474 |  | No action |  | 0.090098824 | 0.0 | 0.00951 | 0.602 |  |  | 0.0
93 | 75396f1857fe480fb7d632308928c2f0 | 37 STRD_AA_2.532 |  | No action |  | 0.05517776256 | 0.0 | 0.009723 | 0.9 |  |  | 0.0
94 | 381086e9ee5c4a65a8b2e31cb012864b | CON LAY_AA_2.532 |  | No action |  | 0.0863705968 | 0.0 | 0.009723 | 0.91 |  |  | 0.0
95 | 0dc9e5c2aceb4ea4ae2e402886a7880f | 26/7_ACSR_2.814 |  | No action |  | 0.08003261056 | 0.0 | 0.01143 | 0.9 |  |  | 0.0
96 | 0fdf9119ebfc4954b195e9b944941038 | 30/19_ACSR_2.896 |  | No action |  | 0.08003261056 | 0.0 | 0.011979 | 0.72 |  |  | 0.0
97 | a7b53413d2e3471aa4fc8901aeed3971 | 54/7_ACSR_2.776 |  | No action |  | 0.08562495136 | 0.0 | 0.011217 | 900.0 |  |  | 0.0
98 | 84bee618109e45b68c060d5caf779db6 | CLASS A_AA_2.606 |  | No action |  | 0.0813996272 | 0.0 | 0.009997 | 720.0 |  |  | 0.0

## overhead_line_types
idtag | name | code | action | comment | earth_resistivity | frequency | Imax | Vnom | wires_in_tower

## underground_cable_types
| idtag | name | code | action | comment | Imax | Vnom | R | X | B | R0 | X0 | B0
0 | 2feaae46c71a41cb8bb15377e74cec7a | BD-FPE AL2-4x5 0.60 kV |  | No action |  | 1.8 | 1.0 | 0.00217 | 0.0014 | 0.0 | 0.052 | 0.087 | 0.0
1 | b6878b9c34ae43dfa32e5fb3bc6f6db6 | BD-FPE AL2-4x6 0.60 kV |  | No action |  | 2.2 | 1.0 | 0.00194 | 0.00131 | 0.0 | 0.243 | 0.149 | 0.0
2 | 6d2d3292d4204253b7ea8ccecc3e1fa2 | BD-FPE AL4-4x4 0.60 kV |  | No action |  | 2.6 | 1.0 | 0.0014 | 0.001 | 0.0 | 0.173 | 0.123 | 0.0
3 | dbae28c260444fbda2301f381b5b1816 | BD-FPE AL4-4x6 0.60 kV |  | No action |  | 3.6 | 1.0 | 0.00089 | 0.00071 | 0.0 | 0.173 | 0.123 | 0.0
4 | cb1a377232bf407da2814edc58bbdad0 | BD-FPE CU2-4x4 0.60 kV |  | No action |  | 2.0 | 1.0 | 0.00168 | 0.00156 | 0.0 | 0.084 | 0.132 | 0.0
5 | b3f784b162274ccdbcbe10cb643b5cdf | BD-FPE CU2-4x5 0.60 kV |  | No action |  | 2.3 | 1.0 | 0.00133 | 0.00137 | 0.0 | 0.084 | 0.132 | 0.0
6 | c19119e7caf44c4fbdb8f925dc39b6f2 | BD-FPE CU2-4x6 0.60 kV |  | No action |  | 2.66 | 1.0 | 0.00122 | 0.00126 | 0.0 | 0.091 | 0.093 | 0.0
7 | f845dc6dbdbb4b5c9a08d32e99ef5176 | BD-FPE CU4-4x4 0.60 kV |  | No action |  | 3.56 | 1.0 | 0.00069 | 0.00101 | 0.0 | 0.06 | 0.068 | 0.0
8 | f7cd40efe0d54361aa3103a42c250cc9 | BD-FPE CU4-4x5 0.60 kV |  | No action |  | 4.55 | 1.0 | 0.00079 | 0.00076 | 0.0 | 0.06 | 0.06 | 0.0
9 | f079e781a04a43fdb9e35ebf7fd29107 | BD-IBER BB3000CU 1.00 kV |  | No action |  | 3.0 | 1.0 | 0.015 | 0.008 | 0.0 | 0.094 | 0.17 | 0.0
10 | 0cfa1ce2f59447dfba4d7c767135a385 | BD-IBER BV2500AL 1.00 kV |  | No action |  | 2.5 | 1.0 | 0.02 | 0.015 | 0.0 | 0.125 | 0.319 | 0.0
11 | 352aff5d8af14f2fa484c606147420d6 | BD-KLOE-M LD1. 1.00 kV |  | No action |  | 1.0 | 1.0 | 0.047 | 0.034 | 0.0 | 0.185 | 0.182 | 0.0
12 | 05f9b70e84994d759b445449440939d1 | BD-KLOE-M LD2. 1.00 kV |  | No action |  | 1.25 | 1.0 | 0.044 | 0.034 | 0.0 | 0.183 | 0.18 | 0.0
13 | 04a41826a0e54a0fb36c7980e4988b14 | BD-KLOE-M LD2.CU 1.00 kV |  | No action |  | 1.55 | 1.0 | 0.029 | 0.045 | 0.0 | 0.124 | 0.164 | 0.0
14 | dcb427035b004cc6a5a5ed61562786a0 | BD-KLOE-M LD3. 1.00 kV |  | No action |  | 1.6 | 1.0 | 0.036 | 0.031 | 0.0 | 0.137 | 0.138 | 0.0
15 | 5adab29cf3b142458ae92894eaf0aef7 | BD-KLOE-M LD3.CU 1.00 kV |  | No action |  | 2.05 | 1.0 | 0.024 | 0.037 | 0.0 | 0.084 | 0.132 | 0.0
16 | b8174fd3095e49ebba3a45a95b8b39d9 | BD-KLOE-M LD4. 1.00 kV |  | No action |  | 2.5 | 1.0 | 0.026 | 0.027 | 0.0 | 0.147 | 0.094 | 0.0
17 | 0eaa574745054d9e8c27df529be520c7 | BD-KLOE-M LD4.CU 1.00 kV |  | No action |  | 2.7 | 1.0 | 0.017 | 0.028 | 0.0 | 0.091 | 0.093 | 0.0
18 | c6b71e398d884ecfa8e277e3d3d417e1 | BD-KLOE-M LD5. 1.00 kV |  | No action |  | 3.1 | 1.0 | 0.017 | 0.022 | 0.0 | 0.11 | 0.077 | 0.0
19 | 850dcd236d0c42cbb243290892eb7c85 | BD-KLOE-M LD5.CU 1.00 kV |  | No action |  | 3.5 | 1.0 | 0.01 | 0.014 | 0.0 | 0.06 | 0.068 | 0.0
20 | 7567a2d83f6d42eca680490c8b0b2482 | BD-KLOE-M LDA1 1.00 kV |  | No action |  | 1.1 | 1.0 | 0.08 | 0.051 | 0.0 | 0.078 | 0.087 | 0.0
21 | a02f25ee4163413ea8e0d9bad4782923 | BD-KLOE-M LDA2 1.00 kV |  | No action |  | 1.25 | 1.0 | 0.048 | 0.046 | 0.0 | 0.052 | 0.087 | 0.0
22 | 3c06dc7214504df6bfeebe4717c8fdd1 | BD-KLOE-M LDA3 1.00 kV |  | No action |  | 1.6 | 1.0 | 0.043 | 0.043 | 0.0 | 0.052 | 0.087 | 0.0
23 | f7de0b2ba0104d6999eadbdc07ce8661 | BD-KLOE-M LDA4 1.00 kV |  | No action |  | 2.0 | 1.0 | 0.039 | 0.028 | 0.0 | 0.243 | 0.149 | 0.0
24 | 27a2805831aa4b7f876d0779274076d8 | BD-KLOE-M LDA5 1.00 kV |  | No action |  | 2.5 | 1.0 | 0.021 | 0.021 | 0.0 | 0.173 | 0.123 | 0.0
25 | 52812b76d20748e49284c0d954c40ea5 | BD-KLOE-M LDA6 1.00 kV |  | No action |  | 3.0 | 1.0 | 0.021 | 0.023 | 0.0 | 0.173 | 0.123 | 0.0
26 | 347f79a09fdc422cbf43f3abe7ccce08 | BD-KLOE-M LDA7 1.00 kV |  | No action |  | 3.7 | 1.0 | 0.017 | 0.02 | 0.0 | 0.121 | 0.098 | 0.0
27 | 8054531b78f5481faf832d13e3742529 | BD-KLOE-M LDC2 1.00 kV |  | No action |  | 2.0 | 1.0 | 0.03 | 0.044 | 0.0 | 0.035 | 0.084 | 0.0
28 | c1613b428a974c879712b33a3f72650d | BD-KLOE-M LDC3 1.00 kV |  | No action |  | 2.6 | 1.0 | 0.022 | 0.036 | 0.0 | 0.028 | 0.071 | 0.0
29 | cc9cf826c41043e5996e040a9da48da6 | BD-KLOE-M LDC6 1.00 kV |  | No action |  | 3.4 | 1.0 | 0.017 | 0.024 | 0.0 | 0.104 | 0.113 | 0.0
30 | 4843bd43bb634ced95baf4b70cae2782 | BD-KLOE-M LDC7 1.00 kV |  | No action |  | 4.4 | 1.0 | 0.013 | 0.017 | 0.0 | 0.018 | 0.036 | 0.0
31 | 885de7d0d7b8431e96e7cce8933b4334 | BD-OTTERM U1250 0.66 kV |  | No action |  | 1.25 | 1.0 | 0.044 | 0.054 | 0.0 | 0.052 | 0.087 | 0.0
32 | 8b3a63c8bae74018bdc1e2ae7707b862 | BD-OTTERM U1600 0.66 kV |  | No action |  | 1.6 | 1.0 | 0.031 | 0.042 | 0.0 | 0.052 | 0.087 | 0.0
33 | 21011c3e08aa47659d29c53928b20899 | BD-OTTERM U2000 0.66 kV |  | No action |  | 2.0 | 1.0 | 0.024 | 0.036 | 0.0 | 0.243 | 0.149 | 0.0
34 | 9389de7fd4cf4753b356e37ca3bf08e0 | BD-OTTERM U2500 0.66 kV |  | No action |  | 2.5 | 1.0 | 0.02 | 0.033 | 0.0 | 0.173 | 0.123 | 0.0
35 | f418fa185a5345b2b0a17d9c971d5919 | BD-OTTERM U3500 0.66 kV |  | No action |  | 3.5 | 1.0 | 0.013 | 0.018 | 0.0 | 0.035 | 0.084 | 0.0
36 | da2a75abf6054c3db293b592fd4f7340 | BD-TELEM KHF-14 0.75 kV |  | No action |  | 1.0 | 1.0 | 0.084 | 0.035 | 0.0 | 0.06 | 0.06 | 0.0
37 | c9b28500f28742b7bc44f2cb75838ea3 | BD-TELEM KHF-16 0.75 kV |  | No action |  | 1.2 | 1.0 | 0.057 | 0.035 | 0.0 | 0.158 | 0.157 | 0.0
38 | e43ec6a81571419db2fd1c8c809df874 | BD-TELEM KHF-18 0.75 kV |  | No action |  | 1.45 | 1.0 | 0.042 | 0.035 | 0.0 | 0.122 | 0.157 | 0.0
39 | 5a766b1aefb245a8b32f7d763cd8c49e | BD-TELEM KHF-26 0.75 kV |  | No action |  | 2.2 | 1.0 | 0.028 | 0.016 | 0.0 | 0.078 | 0.059 | 0.0
40 | f90dbd2da70d431f95951897e8d45a6b | BD-TELEM KHF-28 0.75 kV |  | No action |  | 2.5 | 1.0 | 0.021 | 0.016 | 0.0 | 0.06 | 0.059 | 0.0
41 | 8a853ab5a0494a559536bf7e1d0ca1fe | BD-TELEM KHF-36 0.75 kV |  | No action |  | 3.0 | 1.0 | 0.019 | 0.01 | 0.0 | 0.052 | 0.033 | 0.0
42 | c5970ca805354f74ba596fbdf89fde6d | BD-TELEM KHF-38 0.75 kV |  | No action |  | 3.4 | 1.0 | 0.014 | 0.01 | 0.0 | 0.04 | 0.033 | 0.0
43 | 7524203a15ba4c41a17a5c73ae79a601 | BD-TELEM KHF-46 0.75 kV |  | No action |  | 4.0 | 1.0 | 0.014 | 0.007 | 0.0 | 0.039 | 0.024 | 0.0
44 | 7691b7b175cc4ccebf5d883db1ab0916 | BD-TELEM KHF-48 0.75 kV |  | No action |  | 4.5 | 1.0 | 0.01 | 0.007 | 0.0 | 0.03 | 0.024 | 0.0
45 | d693e102c9ad47f68af5ac99a034aacc | BD-TELEM KHF-56 0.75 kV |  | No action |  | 5.0 | 1.0 | 0.011 | 0.005 | 0.0 | 0.03 | 0.019 | 0.0
46 | 297207dd4a294a02a090fbf3de88294b | BD-TELEM KHF-58 0.75 kV |  | No action |  | 5.5 | 1.0 | 0.008 | 0.005 | 0.0 | 0.023 | 0.019 | 0.0
47 | 954ebe4d3bc440f09f241fdde593d07d | DROSS 1 6.00 kV |  | No action |  | 1.0 | 1.0 | 0.0276 | 0.2758 | 0.0 | 0.001 | 0.0 | 0.0
48 | c521fabc427d4258a1ed1c280779c5bd | EIAJB 3x120 15.00 kV |  | No action |  | 0.283 | 1.0 | 0.153 | 0.11 | 0.0 | 1.0 | 1.0 | 0.0
49 | 7836607986eb4e6f825ea4f2496e2d38 | EIAJB 3x150 15.00 kV |  | No action |  | 0.316 | 1.0 | 0.124 | 0.106 | 0.0 | 1.0 | 1.0 | 0.0
50 | 7e9ede3b0989450ab1686ca868a272a6 | EIAJB 3x185 15.00 kV |  | No action |  | 0.358 | 1.0 | 0.0991 | 0.103 | 0.0 | 1.0 | 1.0 | 0.0
51 | 23fb1f1c4b974f93a08c381e43d26fc6 | EIAJB 3x240 15.00 kV |  | No action |  | 0.416 | 1.0 | 0.0754 | 0.101 | 0.0 | 1.0 | 1.0 | 0.0
52 | 30009eef151f4ed582ffaffe2975157a | EIAJB 3x25 15.00 kV |  | No action |  | 0.12 | 1.0 | 0.727 | 0.143 | 0.0 | 1.0 | 1.0 | 0.0
53 | 7f3afb2220c2426da7c5fdd93c8d6c6f | EIAJB 3x35 15.00 kV |  | No action |  | 0.144 | 1.0 | 0.524 | 0.136 | 0.0 | 1.0 | 1.0 | 0.0
54 | 63195b8be5c64509873ce20da827c771 | EIAJB 3x50 15.00 kV |  | No action |  | 0.171 | 1.0 | 0.367 | 0.129 | 0.0 | 1.0 | 1.0 | 0.0
55 | 6d7dd0252662484db8020e30608149a2 | EIAJB 3x70 15.00 kV |  | No action |  | 0.209 | 1.0 | 0.268 | 0.123 | 0.0 | 1.0 | 1.0 | 0.0
56 | ff19b25b767241cfa11c9dea49009c17 | EIAJB 3x95 15.00 kV |  | No action |  | 0.249 | 1.0 | 0.193 | 0.113 | 0.0 | 1.0 | 1.0 | 0.0
57 | d6b5e40cb0e642e3bfe783d2cc63e53e | KUP 1 6.00 kV |  | No action |  | 1.2 | 1.0 | 0.001 | 0.001 | 0.0 | 0.001 | 0.001 | 0.0
58 | 890a79295a3141709c61b58e1e6bce8a | KUP 1 25.00 kV |  | No action |  | 1.2 | 1.0 | 0.001 | 0.001 | 0.0 | 0.001 | 0.001 | 0.0
59 | 2f1cc824866a49fda7a2b967bd7fc88c | N2XS2Y 1x120 20.00 kV |  | No action |  | 0.368 | 1.0 | 0.153 | 0.125 | 0.0 | 1.003 | 0.546 | 0.0
60 | 48fb5a0b6c0940768a91afc01fe6a1a4 | N2XS2Y 1x150 20.00 kV |  | No action |  | 0.41 | 1.0 | 0.124 | 0.121 | 0.0 | 0.765 | 0.297 | 0.0
61 | 756ddc0f7a8a485592ad7cd992f72c72 | N2XS2Y 1x185 20.00 kV |  | No action |  | 0.462 | 1.0 | 0.0991 | 0.117 | 0.0 | 0.739 | 0.294 | 0.0
62 | bc16b31a727443579ef710ae7fcc5408 | N2XS2Y 1x240 20.00 kV |  | No action |  | 0.534 | 1.0 | 0.0754 | 0.112 | 0.0 | 0.715 | 0.291 | 0.0
63 | dbe74915920a4711bd2f649ed4ae86fb | N2XS2Y 1x25 20.00 kV |  | No action |  | 0.159 | 1.0 | 0.727 | 0.16 | 0.0 | 1.588 | 0.572 | 0.0
64 | 59d3ee6303734f7eaf39513fbc8d813d | N2XS2Y 1x35 20.00 kV |  | No action |  | 0.189 | 1.0 | 0.524 | 0.152 | 0.0 | 1.383 | 0.566 | 0.0
65 | e2ec97f564e649a8952a65778ec29745 | N2XS2Y 1x50 20.00 kV |  | No action |  | 0.223 | 1.0 | 0.387 | 0.145 | 0.0 | 1.244 | 0.56 | 0.0
66 | c7da5a0f8aa8461fa1cdee9661014ce2 | N2XS2Y 1x70 20.00 kV |  | No action |  | 0.272 | 1.0 | 0.268 | 0.137 | 0.0 | 1.122 | 0.554 | 0.0
67 | 037ad92c61ba473aa30a21315881a723 | N2XS2Y 1x95 20.00 kV |  | No action |  | 0.324 | 1.0 | 0.193 | 0.13 | 0.0 | 1.045 | 0.549 | 0.0
68 | fa0903f833eb44b4b8008d84c4130475 | N2XSY 1X500 10kV DE |  | No action |  | 0.739 | 1.0 | 0.046 | 0.096 | 0.0 | 1.0 | 1.0 | 0.0
69 | 96d3b6c363f141bca36dd68f3dd81889 | N2XSY 1x120 10.00 kV |  | No action |  | 0.364 | 1.0 | 0.154 | 0.117 | 0.0 | 1.009 | 0.533 | 0.0
70 | 7a873acacf9e40bc952a26588cef695c | N2XSY 1x120 20.00 kV |  | No action |  | 0.368 | 1.0 | 0.154 | 0.125 | 0.0 | 1.003 | 0.546 | 0.0
71 | 234e27725f67432ca3ab915130c12407 | N2XSY 1x150 10.00 kV |  | No action |  | 0.405 | 1.0 | 0.127 | 0.113 | 0.0 | 0.767 | 0.285 | 0.0
72 | 24246476d89b40cebf7b13a53f6bfa04 | N2XSY 1x150 20.00 kV |  | No action |  | 0.41 | 1.0 | 0.127 | 0.121 | 0.0 | 0.765 | 0.297 | 0.0
73 | 34d9cd638f86456580afe27b581fd03e | N2XSY 1x185 10.00 kV |  | No action |  | 0.457 | 1.0 | 0.103 | 0.11 | 0.0 | 0.742 | 0.283 | 0.0
74 | 0f8bbb4ff82c4a6f8fd50dd6c7c42e05 | N2XSY 1x185 20.00 kV |  | No action |  | 0.463 | 1.0 | 0.102 | 0.117 | 0.0 | 0.739 | 0.294 | 0.0
75 | b613ad950ab04d8abd81827d968fa5c7 | N2XSY 1x240 10.00 kV |  | No action |  | 0.528 | 1.0 | 0.08 | 0.105 | 0.0 | 0.717 | 0.281 | 0.0
76 | 8e996bc3e0af442fb25db24bcdb347b7 | N2XSY 1x240 20.00 kV |  | No action |  | 0.534 | 1.0 | 0.08 | 0.112 | 0.0 | 0.715 | 0.291 | 0.0
77 | a9b5389ef3a8442c95c2cdc9c0f6f63e | N2XSY 1x25 10.00 kV |  | No action |  | 0.157 | 1.0 | 0.711 | 0.149 | 0.0 | 1.595 | 0.555 | 0.0
78 | ecb013b1a2a349ac867d8abd603b3b41 | N2XSY 1x25 20.00 kV |  | No action |  | 0.159 | 1.0 | 0.711 | 0.16 | 0.0 | 1.588 | 0.572 | 0.0
79 | a13f46a5ee614f60953648bf4b200d4a | N2XSY 1x300 10.00 kV |  | No action |  | 0.593 | 1.0 | 0.065 | 0.102 | 0.0 | 0.7 | 0.279 | 0.0
80 | 80a14b1fff2c4678851d528eb5765242 | N2XSY 1x300 20.00 kV |  | No action |  | 0.601 | 1.0 | 0.065 | 0.109 | 0.0 | 0.698 | 0.289 | 0.0
81 | 277825340dd4490b996e4e1096021051 | N2XSY 1x35 10.00 kV |  | No action |  | 0.187 | 1.0 | 0.518 | 0.142 | 0.0 | 1.39 | 0.549 | 0.0
82 | aefa3f67de604fc2b0cfe39b6dd40d80 | N2XSY 1x35 20.00 kV |  | No action |  | 0.189 | 1.0 | 0.518 | 0.152 | 0.0 | 1.383 | 0.566 | 0.0
83 | 2085123378b340119ca40b1de6bde20a | N2XSY 1x400 10.00 kV |  | No action |  | 0.665 | 1.0 | 0.055 | 0.098 | 0.0 | 0.536 | 0.525 | 0.0
84 | d4d154b131fc47fb856a1965632d50bf | N2XSY 1x400 20.00 kV |  | No action |  | 0.674 | 1.0 | 0.054 | 0.105 | 0.0 | 0.535 | 0.179 | 0.0
85 | 8a804e00d114484a95dc35d95e99279f | N2XSY 1x50 10.00 kV |  | No action |  | 0.22 | 1.0 | 0.383 | 0.135 | 0.0 | 1.251 | 0.544 | 0.0
86 | 2f0db3fac927486782b871c6433789cc | N2XSY 1x50 20.00 kV |  | No action |  | 0.223 | 1.0 | 0.382 | 0.145 | 0.0 | 1.244 | 0.56 | 0.0
87 | 321426b73bc149f1a3d8bc32c8854e86 | N2XSY 1x500 20.00 kV |  | No action |  | 0.75 | 1.0 | 0.045 | 0.102 | 0.0 | 0.524 | 0.177 | 0.0
88 | 4358cc04ce9c4c3a90f3458bca17128a | N2XSY 1x70 10.00 kV |  | No action |  | 0.269 | 1.0 | 0.266 | 0.127 | 0.0 | 1.129 | 0.539 | 0.0
89 | 6ef7e268050f45b19955b2c2534d0710 | N2XSY 1x70 20.00 kV |  | No action |  | 0.273 | 1.0 | 0.265 | 0.137 | 0.0 | 1.122 | 0.554 | 0.0
90 | 869f266346a146a2898c7c62b2e2aa1c | N2XSY 1x95 10.00 kV |  | No action |  | 0.321 | 1.0 | 0.193 | 0.122 | 0.0 | 1.051 | 0.536 | 0.0
91 | 1444c817f6064b5ba7729bdeb88c95c4 | N2XSY 1x95 20.00 kV |  | No action |  | 0.325 | 1.0 | 0.192 | 0.13 | 0.0 | 1.045 | 0.549 | 0.0
92 | aa14abf37dcb42c7b07ff6d447e1a860 | N2XSY 3x120 10.00 kV |  | No action |  | 0.349 | 1.0 | 0.155 | 0.092 | 0.0 | 1.0 | 1.0 | 0.0
93 | f277809dee3a4a7a8885339ee2a6921e | N2XSY 3x150 10.00 kV |  | No action |  | 0.392 | 1.0 | 0.126 | 0.09 | 0.0 | 1.0 | 1.0 | 0.0
94 | c83f64a6d9e0412da827d938fe20b4a4 | N2XSY 3x185 10.00 kV |  | No action |  | 0.443 | 1.0 | 0.102 | 0.087 | 0.0 | 1.0 | 1.0 | 0.0
95 | e86dcf2aad8247dbbf8fdfaa1ddd1b45 | N2XSY 3x240 10.00 kV |  | No action |  | 0.513 | 1.0 | 0.078 | 0.084 | 0.0 | 1.0 | 1.0 | 0.0
96 | 2ff4691be8d04447bccb15eada1d372f | N2XSY 3x300 10.00 kV |  | No action |  | 0.579 | 1.0 | 0.063 | 0.082 | 0.0 | 1.0 | 1.0 | 0.0
97 | 2944a27520ed4b06858b8a1b22ce3c47 | N2XSY 3x35 10.00 kV |  | No action |  | 0.178 | 1.0 | 0.525 | 0.111 | 0.0 | 1.0 | 1.0 | 0.0
98 | afe61ba02f7b49b0b2301bf03e604622 | N2XSY 3x50 10.00 kV |  | No action |  | 0.21 | 1.0 | 0.387 | 0.106 | 0.0 | 1.0 | 1.0 | 0.0
99 | 3b66a0cd4e9e46f795373774494b877e | N2XSY 3x70 10.00 kV |  | No action |  | 0.256 | 1.0 | 0.269 | 0.1 | 0.0 | 1.0 | 1.0 | 0.0
100 | 1b9094ca6d504e1098027f2273ddce0b | N2XSY 3x95 10.00 kV |  | No action |  | 0.307 | 1.0 | 0.194 | 0.095 | 0.0 | 1.0 | 1.0 | 0.0
101 | b5a7a1ffeeb047da83ce1db9c0e56512 | N2YSY 1x120 20.00 kV |  | No action |  | 0.343 | 1.0 | 0.153 | 0.125 | 0.0 | 1.0 | 1.0 | 0.0
102 | 03a1d59dc24e4c228c0ce294cfedf066 | N2YSY 1x150 20.00 kV |  | No action |  | 0.381 | 1.0 | 0.127 | 0.121 | 0.0 | 1.0 | 1.0 | 0.0
103 | f12c857fd91840a6a563fc3534a2983d | N2YSY 1x185 20.00 kV |  | No action |  | 0.43 | 1.0 | 0.103 | 0.117 | 0.0 | 1.0 | 1.0 | 0.0
104 | afa6a9aaf18a4c7bbdcebc2739343c5d | N2YSY 1x240 20.00 kV |  | No action |  | 0.496 | 1.0 | 0.079 | 0.112 | 0.0 | 1.0 | 1.0 | 0.0
105 | df4a85a04ce14e2eb02cec26c70b65e9 | N2YSY 1x25 20.00 kV |  | No action |  | 0.148 | 1.0 | 0.711 | 0.16 | 0.0 | 1.0 | 1.0 | 0.0
106 | 5987a3c13af941e1b15802a7c3e30e54 | N2YSY 1x300 20.00 kV |  | No action |  | 0.556 | 1.0 | 0.065 | 0.109 | 0.0 | 1.0 | 1.0 | 0.0
107 | 465c28f540034671a7d9cb4c0a909fa6 | N2YSY 1x35 20.00 kV |  | No action |  | 0.176 | 1.0 | 0.517 | 0.152 | 0.0 | 1.0 | 1.0 | 0.0
108 | a5decc168cec4de192c272773864f83e | N2YSY 1x400 20.00 kV |  | No action |  | 0.623 | 1.0 | 0.055 | 0.105 | 0.0 | 1.0 | 1.0 | 0.0
109 | e96c521949ed4446a71f3ff28e674ed6 | N2YSY 1x50 20.00 kV |  | No action |  | 0.208 | 1.0 | 0.382 | 0.145 | 0.0 | 1.0 | 1.0 | 0.0
110 | efaf5ec7276d402bacb974180de5321a | N2YSY 1x500 20.00 kV |  | No action |  | 0.692 | 1.0 | 0.046 | 0.102 | 0.0 | 1.0 | 1.0 | 0.0
111 | 00221547815a4d7a87a58fc7e3143949 | N2YSY 1x70 20.00 kV |  | No action |  | 0.254 | 1.0 | 0.265 | 0.137 | 0.0 | 1.0 | 1.0 | 0.0
112 | acc3ffba65a6444c9aa1509975a6305c | N2YSY 1x95 20.00 kV |  | No action |  | 0.302 | 1.0 | 0.193 | 0.13 | 0.0 | 1.0 | 1.0 | 0.0
113 | d1a9cb95beee40f2bc3364f3d018c2f3 | NA2XSY 1x120 10.00 kV |  | No action |  | 0.283 | 1.0 | 0.251 | 0.117 | 0.0 | 1.069 | 0.548 | 0.0
114 | e97a06680d0e423eb98f16641026b284 | NA2XSY 1x120 20.00 kV |  | No action |  | 0.287 | 1.0 | 0.251 | 0.125 | 0.0 | 1.065 | 0.56 | 0.0
115 | ab33395199d245b8a7b5638b10fcbeda | NA2XSY 1x150 10.00 kV |  | No action |  | 0.316 | 1.0 | 0.207 | 0.113 | 0.0 | 0.833 | 0.293 | 0.0
116 | 068a3c2f892c4cebbac7393e94188466 | NA2XSY 1x150 20.00 kV |  | No action |  | 0.32 | 1.0 | 0.207 | 0.121 | 0.0 | 0.832 | 0.309 | 0.0
117 | fb6d3cc7ad49468a92c2dec3930dce1f | NA2XSY 1x185 10.00 kV |  | No action |  | 0.358 | 1.0 | 0.166 | 0.11 | 0.0 | 0.791 | 0.296 | 0.0
118 | 1a94cc3c7cc047c0846cee8e69ca7da8 | NA2XSY 1x185 20.00 kV |  | No action |  | 0.362 | 1.0 | 0.166 | 0.117 | 0.0 | 0.789 | 0.306 | 0.0
119 | 40836d95ddb645c69ec717d2b404ca0c | NA2XSY 1x240 10.00 kV |  | No action |  | 0.416 | 1.0 | 0.128 | 0.105 | 0.0 | 0.751 | 0.293 | 0.0
120 | d21b193deeb1482da4597939e13ad9a9 | NA2XSY 1x240 20.00 kV |  | No action |  | 0.421 | 1.0 | 0.127 | 0.112 | 0.0 | 0.749 | 0.303 | 0.0
121 | b95773b2f38842daaecacc3b72c5b464 | NA2XSY 1x300 10.00 kV |  | No action |  | 0.469 | 1.0 | 0.104 | 0.102 | 0.0 | 0.725 | 0.291 | 0.0
122 | ca2e3aaa27fb4148a49498de9ec551df | NA2XSY 1x300 20.00 kV |  | No action |  | 0.474 | 1.0 | 0.102 | 0.109 | 0.0 | 0.724 | 0.301 | 0.0
123 | c1f6933994a946c2897ef1cca0ea729d | NA2XSY 1x35 10.00 kV |  | No action |  | 0.144 | 1.0 | 0.859 | 0.142 | 0.0 | 1.691 | 0.566 | 0.0
124 | 2bf92828b3ea47a99b98e99bb8a45db7 | NA2XSY 1x35 20.00 kV |  | No action |  | 0.146 | 1.0 | 0.859 | 0.152 | 0.0 | 1.686 | 0.581 | 0.0
125 | 7f873292687040fb9f9c937f1606ddb0 | NA2XSY 1x400 10.00 kV |  | No action |  | 0.532 | 1.0 | 0.083 | 0.098 | 0.0 | 0.56 | 0.179 | 0.0
126 | 6354427e92e645caa13909b724889415 | NA2XSY 1x400 20.00 kV |  | No action |  | 0.538 | 1.0 | 0.083 | 0.105 | 0.0 | 0.56 | 0.186 | 0.0
127 | d48ebc1656ef4ac18e7958edb61742cf | NA2XSY 1x50 10.00 kV |  | No action |  | 0.171 | 1.0 | 0.632 | 0.135 | 0.0 | 1.462 | 0.561 | 0.0
128 | 70e74ac0caed479d9f9cbe31ee91c308 | NA2XSY 1x50 20.00 kV |  | No action |  | 0.173 | 1.0 | 0.631 | 0.145 | 0.0 | 1.458 | 0.575 | 0.0
129 | 209ea8f3efd24e87806fe667c5dc2ba8 | NA2XSY 1x500 10.00 kV |  | No action |  | 0.599 | 1.0 | 0.068 | 0.096 | 0.0 | 0.543 | 0.177 | 0.0
130 | 884db5fc2e304275a1f21d0045b3cf0e | NA2XSY 1x500 20.00 kV |  | No action |  | 0.606 | 1.0 | 0.068 | 0.102 | 0.0 | 0.542 | 0.184 | 0.0
131 | 8ff55f0dedea4c9f8938dae482056b7c | NA2XSY 1x70 10.00 kV |  | No action |  | 0.209 | 1.0 | 0.438 | 0.127 | 0.0 | 1.262 | 0.555 | 0.0
132 | 5b4e2a2687014e8aa66b0f81bc938b65 | NA2XSY 1x70 20.00 kV |  | No action |  | 0.211 | 1.0 | 0.438 | 0.137 | 0.0 | 1.258 | 0.568 | 0.0
133 | 3b890ce11e134acb890185a6086b2531 | NA2XSY 1x95 10.00 kV |  | No action |  | 0.249 | 1.0 | 0.317 | 0.122 | 0.0 | 1.138 | 0.551 | 0.0
134 | f703e88eefaa423cac7415ed6a95afe7 | NA2XSY 1x95 20.00 kV |  | No action |  | 0.252 | 1.0 | 0.316 | 0.13 | 0.0 | 1.134 | 0.563 | 0.0
135 | a183fc29a1654e4798d38ca6aa1aadfc | NA2XSY 3x120 10.00 kV |  | No action |  | 0.271 | 1.0 | 0.255 | 0.092 | 0.0 | 1.0 | 1.0 | 0.0
136 | d0d436a07b3143fabe6c4f911f258463 | NA2XSY 3x150 10.00 kV |  | No action |  | 0.304 | 1.0 | 0.208 | 0.09 | 0.0 | 1.0 | 1.0 | 0.0
137 | 73377e917cf64cdc89882c79e1befb8a | NA2XSY 3x185 10.00 kV |  | No action |  | 0.345 | 1.0 | 0.166 | 0.087 | 0.0 | 1.0 | 1.0 | 0.0
138 | 34fc7e5b7a0c481691367c6fb8ed0af7 | NA2XSY 3x240 10.00 kV |  | No action |  | 0.401 | 1.0 | 0.127 | 0.084 | 0.0 | 1.0 | 1.0 | 0.0
139 | efffaa36d947442d9549023b33afafc1 | NA2XSY 3x300 10.00 kV |  | No action |  | 0.453 | 1.0 | 0.103 | 0.082 | 0.0 | 1.0 | 1.0 | 0.0
140 | 6e397fcd70954bf6a20441e549cb0c94 | NA2XSY 3x50 10.00 kV |  | No action |  | 0.162 | 1.0 | 0.642 | 0.106 | 0.0 | 1.0 | 1.0 | 0.0
141 | 5e1caf40b45b4941859c2d0382f68495 | NA2XSY 3x70 10.00 kV |  | No action |  | 0.199 | 1.0 | 0.444 | 0.1 | 0.0 | 1.0 | 1.0 | 0.0
142 | 03b3108433234e59877067a3d47700b1 | NA2XSY 3x95 10.00 kV |  | No action |  | 0.238 | 1.0 | 0.321 | 0.095 | 0.0 | 1.0 | 1.0 | 0.0
143 | 140afe22bcde4e62baebf87b5cb0297b | NA2YSY 1x120 20.00 kV |  | No action |  | 0.267 | 1.0 | 0.251 | 0.125 | 0.0 | 1.0 | 1.0 | 0.0
144 | d57e85fe326a4ebaafd6b5e184014043 | NA2YSY 1x150 20.00 kV |  | No action |  | 0.298 | 1.0 | 0.207 | 0.121 | 0.0 | 1.0 | 1.0 | 0.0
145 | a6d913821f0440a0a57ce446fcaccd3f | NA2YSY 1x185 20.00 kV |  | No action |  | 0.337 | 1.0 | 0.166 | 0.117 | 0.0 | 1.0 | 1.0 | 0.0
146 | 219ee818f56f4dd298a5ec9055c5ff4e | NA2YSY 1x240 20.00 kV |  | No action |  | 0.391 | 1.0 | 0.127 | 0.112 | 0.0 | 1.0 | 1.0 | 0.0
147 | 040e59c0fe6a41b181ce89cd5278003e | NA2YSY 1x300 20.00 kV |  | No action |  | 0.44 | 1.0 | 0.104 | 0.109 | 0.0 | 1.0 | 1.0 | 0.0
148 | 3c6453eb83844dd08bc25a2c11448a6d | NA2YSY 1x35 20.00 kV |  | No action |  | 0.136 | 1.0 | 0.869 | 0.152 | 0.0 | 1.0 | 1.0 | 0.0
149 | 79ce0c558e1342de94700eebb5446d0c | NA2YSY 1x400 20.00 kV |  | No action |  | 0.499 | 1.0 | 0.083 | 0.105 | 0.0 | 1.0 | 1.0 | 0.0
150 | 6b79c054722049b89502bd5cfcaa9537 | NA2YSY 1x50 20.00 kV |  | No action |  | 0.161 | 1.0 | 0.631 | 0.145 | 0.0 | 1.0 | 1.0 | 0.0
151 | cfcbe90a11304681bf6bb3ec187caa7e | NA2YSY 1x500 20.00 kV |  | No action |  | 0.562 | 1.0 | 0.068 | 0.102 | 0.0 | 1.0 | 1.0 | 0.0
152 | 0aec0d62c9fd4d94aa7dcb061a1fe7a5 | NA2YSY 1x70 20.00 kV |  | No action |  | 0.197 | 1.0 | 0.438 | 0.137 | 0.0 | 1.0 | 1.0 | 0.0
153 | 0b2eb3d1a8d0477887ec05681ead7e48 | NA2YSY 1x95 20.00 kV |  | No action |  | 0.235 | 1.0 | 0.316 | 0.13 | 0.0 | 1.0 | 1.0 | 0.0
154 | 7013f7e4e93f47aa8b4cfc3f3744ed67 | NAEKEBA 3x120 20.00 kV |  | No action |  | 0.237 | 1.0 | 0.256 | 0.126 | 0.0 | 1.5 | 0.25 | 0.0
155 | 69b6289b98d34a21bfef4548604e9783 | NAEKEBA 3x150 20.00 kV |  | No action |  | 0.267 | 1.0 | 0.21 | 0.122 | 0.0 | 1.4 | 0.22 | 0.0
156 | c8a2d2d1f13845afb97d78cd6ba92446 | NAEKEBA 3x185 20.00 kV |  | No action |  | 0.304 | 1.0 | 0.168 | 0.118 | 0.0 | 1.3 | 0.21 | 0.0
157 | 27500352f6cf4490aa46c7c8ed4ac8c9 | NAEKEBA 3x240 20.00 kV |  | No action |  | 0.355 | 1.0 | 0.13 | 0.114 | 0.0 | 1.21 | 0.2 | 0.0
158 | 5d976c6e1597403f84fbe6991537fe82 | NAEKEBA 3x300 20.00 kV |  | No action |  | 0.403 | 1.0 | 0.106 | 0.111 | 0.0 | 1.0 | 1.0 | 0.0
159 | d125037b656040b09d59f4181118ae9e | NAEKEBA 3x50 20.00 kV |  | No action |  | 0.14 | 1.0 | 0.644 | 0.146 | 0.0 | 2.15 | 0.4 | 0.0
160 | 2db5884f458d42899660f2730afd8d6f | NAEKEBA 3x70 20.00 kV |  | No action |  | 0.173 | 1.0 | 0.446 | 0.137 | 0.0 | 1.95 | 0.35 | 0.0
161 | 8bfc60ef88f0438db8be42be3a2d8ade | NAEKEBA 3x95 20.00 kV |  | No action |  | 0.208 | 1.0 | 0.323 | 0.131 | 0.0 | 1.73 | 0.3 | 0.0
162 | 0d30bef787eb4c7f9a9a2486af21c82d | NAKBA 3x120 10.00 kV |  | No action |  | 0.229 | 1.0 | 0.256 | 0.097 | 0.0 | 2.4 | 1.0 | 0.0
163 | 788efcf13fc24f20801de7771dfd5999 | NAKBA 3x120/70 1.00 kV |  | No action |  | 0.249 | 1.0 | 0.255 | 0.083 | 0.0 | 1.584 | 0.35 | 0.0
164 | ddef2cc2e9544e6287f2e3dd239acbdf | NAKBA 3x150 10.00 kV |  | No action |  | 0.259 | 1.0 | 0.21 | 0.094 | 0.0 | 2.1 | 1.0 | 0.0
165 | 470416a09bb64fb8b6df282532ce2b63 | NAKBA 3x150/70 1.00 kV |  | No action |  | 0.281 | 1.0 | 0.208 | 0.084 | 0.0 | 1.531 | 0.377 | 0.0
166 | 9481572f542b45da8bbae27ff8bab8c7 | NAKBA 3x185 10.00 kV |  | No action |  | 0.295 | 1.0 | 0.168 | 0.092 | 0.0 | 1.8 | 1.0 | 0.0
167 | 28d29a3b5c3043079019d5f294dabe6a | NAKBA 3x185/95 1.00 kV |  | No action |  | 0.32 | 1.0 | 0.167 | 0.083 | 0.0 | 1.124 | 0.361 | 0.0
168 | b593755cd08d429782e97c6a60404903 | NAKBA 3x240 10.00 kV |  | No action |  | 0.343 | 1.0 | 0.13 | 0.089 | 0.0 | 1.48 | 1.0 | 0.0
169 | 3d46b41ebc4a4a47acc497e1565e4546 | NAKBA 3x240/120 1.00 kV |  | No action |  | 0.372 | 1.0 | 0.131 | 0.082 | 0.0 | 0.899 | 0.361 | 0.0
170 | d705b3dd9b7e4ef190796a06bf0fee4e | NAKBA 3x25/16 1.00 kV |  | No action |  | 0.103 | 1.0 | 1.201 | 0.092 | 0.0 | 6.87 | 0.408 | 0.0
171 | f2f788d8f357457fbd3d89773df75bb3 | NAKBA 3x300 10.00 kV |  | No action |  | 0.389 | 1.0 | 0.106 | 0.087 | 0.0 | 1.0 | 1.0 | 0.0
172 | 2d121574d2d8400b89f4fadf81323b42 | NAKBA 3x300/150 1.00 kV |  | No action |  | 0.42 | 1.0 | 0.107 | 0.082 | 0.0 | 0.737 | 0.354 | 0.0
173 | 5a1f42e95f8d40bfb6daa548421ee847 | NAKBA 3x35/16 1.00 kV |  | No action |  | 0.124 | 1.0 | 0.876 | 0.09 | 0.0 | 6.535 | 0.422 | 0.0
174 | 54f63ff103e943a4b2d83278c2115d9b | NAKBA 3x50 10.00 kV |  | No action |  | 0.132 | 1.0 | 0.643 | 0.109 | 0.0 | 3.4 | 1.0 | 0.0
175 | 2774f281c1ff47a198bdcd3f122631f4 | NAKBA 3x50/25 1.00 kV |  | No action |  | 0.148 | 1.0 | 0.642 | 0.087 | 0.0 | 4.237 | 0.397 | 0.0
176 | 6100be6ac2c14850ad2b5c7cb8fb1459 | NAKBA 3x70 10.00 kV |  | No action |  | 0.165 | 1.0 | 0.446 | 0.104 | 0.0 | 3.1 | 1.0 | 0.0
177 | ca6e9bf7c1ea4ed7a1fcbfe9ceb4776d | NAKBA 3x70/35 1.00 kV |  | No action |  | 0.182 | 1.0 | 0.444 | 0.085 | 0.0 | 3.072 | 0.383 | 0.0
178 | 9d4a28011ca144ffa7583e5a29b0f663 | NAKBA 3x95 10.00 kV |  | No action |  | 0.2 | 1.0 | 0.323 | 0.1 | 0.0 | 2.8 | 1.0 | 0.0
179 | 885ad86508734b02b9fd4cf334df2039 | NAKBA 3x95/50 1.00 kV |  | No action |  | 0.218 | 1.0 | 0.321 | 0.084 | 0.0 | 2.237 | 0.367 | 0.0
180 | 9b52ef0a11a44dcc9c7b3d7806ed8063 | NAKBA 4x120 1.00 kV |  | No action |  | 0.249 | 1.0 | 0.255 | 0.085 | 0.0 | 1.02 | 0.299 | 0.0
181 | 347b1d6f9db14f25a55946966cb1ac0c | NAKBA 4x150 1.00 kV |  | No action |  | 0.281 | 1.0 | 0.208 | 0.086 | 0.0 | 0.832 | 0.305 | 0.0
182 | d11fa04aa0704cd78a7e39611d5c1ad6 | NAKBA 4x16 1.00 kV |  | No action |  | 0.079 | 1.0 | 1.891 | 0.099 | 0.0 | 7.564 | 0.401 | 0.0
183 | c7b1dbd81f7b4aab8bb3b7cf500dda84 | NAKBA 4x185 1.00 kV |  | No action |  | 0.32 | 1.0 | 0.167 | 0.085 | 0.0 | 0.668 | 0.298 | 0.0
184 | e59a46761c3c436790060fae9d882291 | NAKBA 4x240 1.00 kV |  | No action |  | 0.372 | 1.0 | 0.131 | 0.084 | 0.0 | 0.524 | 0.295 | 0.0
185 | aa3c1c1ad5414b22a25c603138c69740 | NAKBA 4x25 1.00 kV |  | No action |  | 0.103 | 1.0 | 1.201 | 0.094 | 0.0 | 4.804 | 0.366 | 0.0
186 | a14cfe8b5c934d3891a9ee40adafa39b | NAKBA 4x300 1.00 kV |  | No action |  | 0.42 | 1.0 | 0.107 | 0.084 | 0.0 | 0.428 | 0.289 | 0.0
187 | f6df40c99b6d4b9ab12484bc9b44c8ac | NAKBA 4x35 1.00 kV |  | No action |  | 0.124 | 1.0 | 0.876 | 0.092 | 0.0 | 3.504 | 0.348 | 0.0
188 | 4e1ba090d53a42bfad52506cea2edb7e | NAKBA 4x50 1.00 kV |  | No action |  | 0.148 | 1.0 | 0.642 | 0.09 | 0.0 | 2.568 | 0.332 | 0.0
189 | 3172b7266c654e678263291b69c846b6 | NAKBA 4x70 1.00 kV |  | No action |  | 0.182 | 1.0 | 0.444 | 0.087 | 0.0 | 1.776 | 0.318 | 0.0
190 | cc22537d1fe346818cf8812134f8425b | NAKBA 4x95 1.00 kV |  | No action |  | 0.218 | 1.0 | 0.321 | 0.086 | 0.0 | 1.284 | 0.307 | 0.0
191 | 0e7b7a4e3fe04fb39b614bc5f80f4249 | NAYCWY 4x120/70 1.00 kV |  | No action |  | 0.242 | 1.0 | 0.255 | 0.08 | 0.0 | 1.02 | 0.292 | 0.0
192 | 60d8202e42dd4f01956d1cd8ffd84452 | NAYCWY 4x150/70 1.00 kV |  | No action |  | 0.27 | 1.0 | 0.208 | 0.08 | 0.0 | 0.832 | 0.292 | 0.0
193 | 8c4c94370e0d4e5da7853793516305e6 | NAYCWY 4x185/95 1.00 kV |  | No action |  | 0.308 | 1.0 | 0.167 | 0.08 | 0.0 | 0.668 | 0.292 | 0.0
194 | 73374d16e4d14e0c95fdd4b213b3629b | NAYCWY 4x35/16 1.00 kV |  | No action |  | 0.118 | 1.0 | 0.876 | 0.083 | 0.0 | 3.504 | 0.343 | 0.0
195 | 93ce6ad594b1461ea2527b6d78c2b837 | NAYCWY 4x50/25 1.00 kV |  | No action |  | 0.142 | 1.0 | 0.642 | 0.083 | 0.0 | 2.568 | 0.312 | 0.0
196 | 9421b7af1ce64fc18ddc93ec4f926e89 | NAYCWY 4x70/35 1.00 kV |  | No action |  | 0.176 | 1.0 | 0.444 | 0.082 | 0.0 | 1.776 | 0.3 | 0.0
197 | 741bd985716f4c26a998e19e63b21601 | NAYCWY 4x95/50 1.00 kV |  | No action |  | 0.211 | 1.0 | 0.321 | 0.082 | 0.0 | 1.284 | 0.299 | 0.0
198 | 6a6427d53c2b489e9435acd2cb8bf593 | NAYFGBY 3x120 6.00 kV |  | No action |  | 0.243 | 1.0 | 0.255 | 0.096 | 0.0 | 1.0 | 1.0 | 0.0
199 | f81bdb640706446693e2116ddd15c9a2 | NAYFGBY 3x150 6.00 kV |  | No action |  | 0.274 | 1.0 | 0.208 | 0.093 | 0.0 | 1.0 | 1.0 | 0.0
200 | 6449fefa7e25426cb2b847413f4e2250 | NAYFGBY 3x185 6.00 kV |  | No action |  | 0.31 | 1.0 | 0.167 | 0.091 | 0.0 | 1.0 | 1.0 | 0.0
201 | 26d437e1bf474e599f4fe3308501f5d4 | NAYFGBY 3x240 6.00 kV |  | No action |  | 0.361 | 1.0 | 0.129 | 0.088 | 0.0 | 1.0 | 1.0 | 0.0
202 | 14ada4eb8a704151adb75f7c7a263772 | NAYFGBY 3x300 6.00 kV |  | No action |  | 0.408 | 1.0 | 0.105 | 0.086 | 0.0 | 1.0 | 1.0 | 0.0
203 | 4df20e45af7a4ae6a464fb367860c425 | NAYFGBY 3x50 6.00 kV |  | No action |  | 0.145 | 1.0 | 0.643 | 0.109 | 0.0 | 1.0 | 1.0 | 0.0
204 | 61454da020ab4ca5ae34757cb56fa697 | NAYFGBY 3x70 6.00 kV |  | No action |  | 0.178 | 1.0 | 0.445 | 0.103 | 0.0 | 1.0 | 1.0 | 0.0
205 | 5ac8c7172b664456a9d5d4a727c8deae | NAYFGBY 3x95 6.00 kV |  | No action |  | 0.214 | 1.0 | 0.322 | 0.099 | 0.0 | 1.0 | 1.0 | 0.0
206 | 008fc136245340d09cd3efca9a091303 | NAYSEY 3x300 10.00 kV |  | No action |  | 0.401 | 1.0 | 0.1 | 0.087 | 0.0 | 1.0 | 1.0 | 0.0
207 | 740140bc53dc46719bf38d05373d16a7 | NAYY 4x120 1.00 kV |  | No action |  | 0.242 | 1.0 | 0.255 | 0.08 | 0.0 | 1.02 | 0.292 | 0.0
208 | 7d98606f725a4614bd3af4d54118f3e5 | NAYY 4x150 1.00 kV |  | No action |  | 0.27 | 1.0 | 0.208 | 0.08 | 0.0 | 0.832 | 0.292 | 0.0
209 | 539db55bef244fcfb265705c5707d82e | NAYY 4x185 1.00 kV |  | No action |  | 0.308 | 1.0 | 0.167 | 0.08 | 0.0 | 0.668 | 0.292 | 0.0
210 | b93093bbb89f4ddcb8c8ed1df77358f0 | NAYY 4x35 1.00 kV |  | No action |  | 0.118 | 1.0 | 0.876 | 0.083 | 0.0 | 3.504 | 0.343 | 0.0
211 | 5b5150de95724b5eaf92dfa5b7596e1e | NAYY 4x50 1.00 kV |  | No action |  | 0.142 | 1.0 | 0.642 | 0.083 | 0.0 | 2.568 | 0.312 | 0.0
212 | 87da89733c8a4031bf6244168fadedfd | NAYY 4x70 1.00 kV |  | No action |  | 0.176 | 1.0 | 0.444 | 0.082 | 0.0 | 1.776 | 0.3 | 0.0
213 | e773f8af222f4373af948edc42a97499 | NAYY 4x95 1.00 kV |  | No action |  | 0.211 | 1.0 | 0.321 | 0.082 | 0.0 | 1.284 | 0.299 | 0.0
214 | 02282e87e6e2489eb896c76ec4eaa209 | NEKEBA 3x120 20.00 kV |  | No action |  | 0.304 | 1.0 | 0.157 | 0.126 | 0.0 | 1.4 | 0.25 | 0.0
215 | 3d86fbf85887498ba5e488130f423a3b | NEKEBA 3x150 20.00 kV |  | No action |  | 0.343 | 1.0 | 0.128 | 0.122 | 0.0 | 1.3 | 0.22 | 0.0
216 | 87e660da1ba7475ab2c3ce7194cbad0c | NEKEBA 3x185 20.00 kV |  | No action |  | 0.388 | 1.0 | 0.103 | 0.118 | 0.0 | 1.2 | 0.21 | 0.0
217 | 3d2bc5c61a1140989c8edfda20d132f4 | NEKEBA 3x240 20.00 kV |  | No action |  | 0.453 | 1.0 | 0.081 | 0.114 | 0.0 | 1.15 | 0.2 | 0.0
218 | 4194e2978c1446cbbbd372752bb2d668 | NEKEBA 3x25 20.00 kV |  | No action |  | 0.126 | 1.0 | 0.724 | 0.161 | 0.0 | 1.0 | 1.0 | 0.0
219 | 8552588a62e946a6bc33be6f074bc738 | NEKEBA 3x300 20.00 kV |  | No action |  | 0.511 | 1.0 | 0.066 | 0.111 | 0.0 | 1.0 | 1.0 | 0.0
220 | 6ae3db72c40d4cf1a3e66c6539ad7946 | NEKEBA 3x35 20.00 kV |  | No action |  | 0.151 | 1.0 | 0.526 | 0.153 | 0.0 | 1.0 | 1.0 | 0.0
221 | 3fdd823af7394d839453036fd60aad49 | NEKEBA 3x50 20.00 kV |  | No action |  | 0.18 | 1.0 | 0.39 | 0.146 | 0.0 | 2.0 | 0.4 | 0.0
222 | 75cdf70013214f42b0c12ab6d4610ae2 | NEKEBA 3x70 20.00 kV |  | No action |  | 0.222 | 1.0 | 0.271 | 0.137 | 0.0 | 1.8 | 0.35 | 0.0
223 | 012cd72fcf5a40df9d31890a71e9dd21 | NEKEBA 3x95 20.00 kV |  | No action |  | 0.268 | 1.0 | 0.197 | 0.131 | 0.0 | 1.6 | 0.3 | 0.0
224 | 9bc3733d60de4712904e089cdab02ff2 | NKBA 3X 16 10kV E |  | No action |  | 0.09 | 1.0 | 1.12 | 0.132 | 0.0 | 1.0 | 1.0 | 0.0
225 | 61b813f9f0a94860a84d9bf53b02ccd6 | NKBA 3X 25 10kV E |  | No action |  | 0.117 | 1.0 | 0.714 | 0.122 | 0.0 | 1.0 | 1.0 | 0.0
226 | 1674eabf761543b1bc3277a7be8b1e24 | NKBA 3X 25/ 16 1kV-TN |  | No action |  | 0.133 | 1.0 | 0.724 | 0.092 | 0.0 | 4.148 | 0.408 | 0.0
227 | f4aaafecf28740d38df9ee6f079141c0 | NKBA 3X 25/ 16 1kV-TT |  | No action |  | 0.133 | 1.0 | 0.724 | 0.092 | 0.0 | 1.672 | 1.523 | 0.0
228 | fa3c43bfea9e4e90bdb98e9823d9e590 | NKBA 3x120 10.00 kV |  | No action |  | 0.293 | 1.0 | 0.157 | 0.097 | 0.0 | 2.3 | 1.0 | 0.0
229 | c6fc7f75e2154484a03b66e32cebb150 | NKBA 3x120/70 1.00 kV |  | No action |  | 0.32 | 1.0 | 0.157 | 0.083 | 0.0 | 0.97 | 0.35 | 0.0
230 | 0064f75cb85e4c4c9547e83792221fdd | NKBA 3x150 10.00 kV |  | No action |  | 0.332 | 1.0 | 0.128 | 0.094 | 0.0 | 2.0 | 1.0 | 0.0
231 | cb193f149afc4a32ab2389f72b83ed61 | NKBA 3x150/70 1.00 kV |  | No action |  | 0.361 | 1.0 | 0.127 | 0.084 | 0.0 | 0.927 | 0.377 | 0.0
232 | c8ea3d44620745dbb77c3ec4f7c5f5ee | NKBA 3x185 10.00 kV |  | No action |  | 0.377 | 1.0 | 0.103 | 0.092 | 0.0 | 1.7 | 1.0 | 0.0
233 | 978b127be3b84513af72d99cf43b59bb | NKBA 3x185/95 1.00 kV |  | No action |  | 0.41 | 1.0 | 0.103 | 0.083 | 0.0 | 0.68 | 0.361 | 0.0
234 | 086ee862d5e94de6957e1712d1245078 | NKBA 3x240 10.00 kV |  | No action |  | 0.437 | 1.0 | 0.081 | 0.089 | 0.0 | 1.4 | 1.0 | 0.0
235 | 61e5691e61234ce88324afe02fcb143d | NKBA 3x240/120 1.00 kV |  | No action |  | 0.474 | 1.0 | 0.08 | 0.082 | 0.0 | 0.539 | 0.361 | 0.0
236 | b7140190ded34d74aeea4396595085f2 | NKBA 3x300 10.00 kV |  | No action |  | 0.493 | 1.0 | 0.067 | 0.087 | 0.0 | 1.0 | 1.0 | 0.0
237 | e006dcf1a0ae4047bb4b7199431f3a5f | NKBA 3x300/150 1.00 kV |  | No action |  | 0.533 | 1.0 | 0.066 | 0.082 | 0.0 | 0.442 | 0.354 | 0.0
238 | fdacf93c45974547b8989f160c791714 | NKBA 3x35 10.00 kV |  | No action |  | 0.143 | 1.0 | 0.526 | 0.115 | 0.0 | 1.0 | 1.0 | 0.0
239 | ab18e22d370b486384d7f45f52ea2e0d | NKBA 3x35/16 1.00 kV |  | No action |  | 0.161 | 1.0 | 0.526 | 0.09 | 0.0 | 3.95 | 0.422 | 0.0
240 | b7edce3c6bad4330a9de70789d5c908f | NKBA 3x50 10.00 kV |  | No action |  | 0.171 | 1.0 | 0.39 | 0.109 | 0.0 | 3.2 | 1.0 | 0.0
241 | afdf8cf86f724514b4a1fb114b03cfe4 | NKBA 3x50/25 1.00 kV |  | No action |  | 0.191 | 1.0 | 0.389 | 0.087 | 0.0 | 2.56 | 0.397 | 0.0
242 | 0a2069cf328b4d89b82e4861ba3fd3e3 | NKBA 3x70 10.00 kV |  | No action |  | 0.212 | 1.0 | 0.271 | 0.104 | 0.0 | 2.9 | 1.0 | 0.0
243 | c13a3cf2e3b3487f85385bcc99e24758 | NKBA 3x70/35 1.00 kV |  | No action |  | 0.235 | 1.0 | 0.271 | 0.085 | 0.0 | 1.848 | 0.383 | 0.0
244 | 02e6b16a8ca4489cb4ef1908ed840735 | NKBA 3x95 10.00 kV |  | No action |  | 0.257 | 1.0 | 0.196 | 0.1 | 0.0 | 2.6 | 1.0 | 0.0
245 | 6e34e18012e64f4b9e57766ef09994b7 | NKBA 3x95/50 1.00 kV |  | No action |  | 0.281 | 1.0 | 0.197 | 0.084 | 0.0 | 1.369 | 0.367 | 0.0
246 | c9c5034e2fc64757ac37f529fc0cc80c | NKBA 4x120 1.00 kV |  | No action |  | 0.32 | 1.0 | 0.157 | 0.085 | 0.0 | 0.628 | 0.299 | 0.0
247 | 7e6a2dd8240b42ac8700e0579bb0f0ab | NKBA 4x150 1.00 kV |  | No action |  | 0.361 | 1.0 | 0.125 | 0.086 | 0.0 | 0.5 | 0.305 | 0.0
248 | 791099a69307417981dfcf88b63a1774 | NKBA 4x16 1.00 kV |  | No action |  | 0.105 | 1.0 | 1.141 | 0.099 | 0.0 | 4.564 | 0.401 | 0.0
249 | 3e3c18df47334c788233347581a1f698 | NKBA 4x185 1.00 kV |  | No action |  | 0.41 | 1.0 | 0.101 | 0.085 | 0.0 | 0.404 | 0.298 | 0.0
250 | e19784a7ab86455ea72f753a89b61302 | NKBA 4x240 1.00 kV |  | No action |  | 0.474 | 1.0 | 0.077 | 0.084 | 0.0 | 0.308 | 0.295 | 0.0
251 | 74197644a2974914a6c24b88788b073e | NKBA 4x25 1.00 kV |  | No action |  | 0.133 | 1.0 | 0.724 | 0.094 | 0.0 | 2.896 | 0.366 | 0.0
252 | 938367188a524680b02827ee1e7015a3 | NKBA 4x300 1.00 kV |  | No action |  | 0.533 | 1.0 | 0.063 | 0.084 | 0.0 | 0.252 | 0.289 | 0.0
253 | cd03a07e2cf246f1a7ab1302e6c4e7f6 | NKBA 4x35 1.00 kV |  | No action |  | 0.161 | 1.0 | 0.526 | 0.092 | 0.0 | 2.104 | 0.348 | 0.0
254 | 6b878aafde214fc4bff3f61685bdb765 | NKBA 4x50 1.00 kV |  | No action |  | 0.191 | 1.0 | 0.389 | 0.09 | 0.0 | 1.556 | 0.332 | 0.0
255 | d9682bc2adf84cf7a41a548c0bea7f66 | NKBA 4x70 1.00 kV |  | No action |  | 0.235 | 1.0 | 0.271 | 0.087 | 0.0 | 1.084 | 0.318 | 0.0
256 | d708284cc02b4cda9959a6f360929607 | NKBA 4x95 1.00 kV |  | No action |  | 0.281 | 1.0 | 0.197 | 0.086 | 0.0 | 0.788 | 0.307 | 0.0
257 | d63bb551345648c4b1505906fa0756d7 | NKBA FOR 25.00 kV |  | No action |  | 0.343 | 1.0 | 0.128 | 0.122 | 0.0 | 0.0 | 0.0 | 0.0
258 | 385990512c7c4d2da64ca29beac06c13 | NKBA NOR 25.00 kV |  | No action |  | 0.277 | 1.0 | 1.0 | 1.0 | 0.0 | 0.0 | 0.0 | 0.0
259 | f15214c489554c2abf96eda3b88ec281 | NYCWY 3x120/70 1.00 kV |  | No action |  | 0.313 | 1.0 | 0.157 | 0.072 | 0.0 | 0.975 | 0.122 | 0.0
260 | e55b2b5e2c43445785043770869fcb0d | NYCWY 3x150/70 1.00 kV |  | No action |  | 0.353 | 1.0 | 0.127 | 0.072 | 0.0 | 0.933 | 0.114 | 0.0
261 | 265c011fdd684d6181b67231cfca8a55 | NYCWY 3x185/95 1.00 kV |  | No action |  | 0.399 | 1.0 | 0.103 | 0.072 | 0.0 | 0.694 | 0.107 | 0.0
262 | 3a9d9a8094724be48b193b587a10e378 | NYCWY 3x240/120 1.00 kV |  | No action |  | 0.464 | 1.0 | 0.08 | 0.072 | 0.0 | 0.545 | 0.104 | 0.0
263 | 5e322011c6404f60bf23ff8a2e4b64e0 | NYCWY 3x25/16 1.00 kV |  | No action |  | 0.128 | 1.0 | 0.724 | 0.08 | 0.0 | 4.156 | 0.138 | 0.0
264 | 7988ba96bb094328a50d010a14a48233 | NYCWY 3x300/150 1.00 kV |  | No action |  | 0.524 | 1.0 | 0.066 | 0.072 | 0.0 | 0.447 | 0.1 | 0.0
265 | 5178822a0f1f4b8fa6d4f38845fb9578 | NYCWY 3x35/16 1.00 kV |  | No action |  | 0.157 | 1.0 | 0.526 | 0.077 | 0.0 | 3.95 | 0.128 | 0.0
266 | 9eb91c146c9148cb8fbb31fbe965f11a | NYCWY 3x50/25 1.00 kV |  | No action |  | 0.185 | 1.0 | 0.389 | 0.077 | 0.0 | 2.56 | 0.12 | 0.0
267 | 92c8814f8cfb435884ad641e6968be24 | NYCWY 3x70/35 1.00 kV |  | No action |  | 0.228 | 1.0 | 0.271 | 0.074 | 0.0 | 1.859 | 0.122 | 0.0
268 | abf3cd77185648b892c36865bb8465be | NYCWY 3x95/50 1.00 kV |  | No action |  | 0.275 | 1.0 | 0.197 | 0.074 | 0.0 | 1.373 | 0.122 | 0.0
269 | 9434475805054b8d810651f425d653d5 | NYCWY 4x1.5/1.5 1.00 kV |  | No action |  | 0.026 | 1.0 | 12.1 | 0.115 | 0.0 | 48.4 | 0.459 | 0.0
270 | c44db2b600ae4c4385697f6713c1cbec | NYCWY 4x10/10 1.00 kV |  | No action |  | 0.075 | 1.0 | 1.81 | 0.094 | 0.0 | 7.24 | 0.378 | 0.0
271 | 9b3245acad29408da150091d456ec11f | NYCWY 4x120/70 1.00 kV |  | No action |  | 0.313 | 1.0 | 0.157 | 0.08 | 0.0 | 0.628 | 0.292 | 0.0
272 | 95406726f491448491d7c57a7d2148db | NYCWY 4x150/70 1.00 kV |  | No action |  | 0.353 | 1.0 | 0.125 | 0.08 | 0.0 | 0.5 | 0.292 | 0.0
273 | a6f5b2096cc943c9abcfef47269be45d | NYCWY 4x16/16 1.00 kV |  | No action |  | 0.098 | 1.0 | 1.141 | 0.09 | 0.0 | 4.564 | 0.358 | 0.0
274 | 5e38bdf572df470ab562ed58bf83a0cc | NYCWY 4x185/95 1.00 kV |  | No action |  | 0.399 | 1.0 | 0.101 | 0.08 | 0.0 | 0.404 | 0.292 | 0.0
275 | fc42762be0014c77b923074751d5faf4 | NYCWY 4x2.5/2.5 1.00 kV |  | No action |  | 0.034 | 1.0 | 7.28 | 0.11 | 0.0 | 29.12 | 0.441 | 0.0
276 | 5d00dc7320ab4146adb03b38b6a9b467 | NYCWY 4x240/120 1.00 kV |  | No action |  | 0.464 | 1.0 | 0.077 | 0.079 | 0.0 | 0.308 | 0.29 | 0.0
277 | 395bde98c97d443da8221a805c54e8a9 | NYCWY 4x25/16 1.00 kV |  | No action |  | 0.128 | 1.0 | 0.724 | 0.086 | 0.0 | 2.896 | 0.355 | 0.0
278 | a7f4d138523147d28b7880eeb6e2a84c | NYCWY 4x300/150 1.00 kV |  | No action |  | 0.524 | 1.0 | 0.063 | 0.079 | 0.0 | 0.252 | 0.289 | 0.0
279 | 7c5f1828e3d1401085384863f1dccdd2 | NYCWY 4x35/16 1.00 kV |  | No action |  | 0.157 | 1.0 | 0.526 | 0.083 | 0.0 | 2.104 | 0.314 | 0.0
280 | 1a317cfdc4c1443cb9b064b64b8d657d | NYCWY 4x4/4 1.00 kV |  | No action |  | 0.044 | 1.0 | 4.56 | 0.107 | 0.0 | 18.24 | 0.426 | 0.0
281 | 14895a3741a24245a4478cbfe2f54bb3 | NYCWY 4x50/25 1.00 kV |  | No action |  | 0.185 | 1.0 | 0.389 | 0.083 | 0.0 | 1.556 | 0.312 | 0.0
282 | 17b5acf86c2e408fa2bd659304563d28 | NYCWY 4x6/6 1.00 kV |  | No action |  | 0.056 | 1.0 | 3.03 | 0.1 | 0.0 | 12.12 | 0.403 | 0.0
283 | 94e4ca643b7348fdb6f69aa03ab11fe1 | NYCWY 4x70/35 1.00 kV |  | No action |  | 0.228 | 1.0 | 0.271 | 0.082 | 0.0 | 1.084 | 0.3 | 0.0
284 | cf756b8c67c44a0f960b8d4cd4a76962 | NYCWY 4x95/50 1.00 kV |  | No action |  | 0.275 | 1.0 | 0.197 | 0.082 | 0.0 | 0.788 | 0.299 | 0.0
285 | 2909d94cbac04bbcaee120def80eca55 | NYFGBY 3x120 6.00 kV |  | No action |  | 0.313 | 1.0 | 0.156 | 0.096 | 0.0 | 1.0 | 1.0 | 0.0
286 | 41c5273fe5e1400d9793f0ff431496a9 | NYFGBY 3x150 6.00 kV |  | No action |  | 0.352 | 1.0 | 0.128 | 0.093 | 0.0 | 1.0 | 1.0 | 0.0
287 | 0f1272dac6c648988772f2132d4ee09a | NYFGBY 3x185 6.00 kV |  | No action |  | 0.397 | 1.0 | 0.102 | 0.091 | 0.0 | 1.0 | 1.0 | 0.0
288 | 9ace32b43c2f4b59a1655f3a04733ab1 | NYFGBY 3x240 6.00 kV |  | No action |  | 0.46 | 1.0 | 0.08 | 0.088 | 0.0 | 1.0 | 1.0 | 0.0
289 | 2a21426854a847daaa7bf11ca10fa892 | NYFGBY 3x25 6.00 kV |  | No action |  | 0.126 | 1.0 | 0.724 | 0.12 | 0.0 | 1.0 | 1.0 | 0.0
290 | 2659692ce01547558c364e84054aa402 | NYFGBY 3x300 6.00 kV |  | No action |  | 0.518 | 1.0 | 0.066 | 0.086 | 0.0 | 1.0 | 1.0 | 0.0
291 | c475a3c0a1a84c08bbe86d47cb0fa503 | NYFGBY 3x35 6.00 kV |  | No action |  | 0.158 | 1.0 | 0.525 | 0.114 | 0.0 | 1.0 | 1.0 | 0.0
292 | 2baf7e949183495c8e58d9f5be87f4f6 | NYFGBY 3x50 6.00 kV |  | No action |  | 0.187 | 1.0 | 0.389 | 0.109 | 0.0 | 1.0 | 1.0 | 0.0
293 | 491806ce71ae4e8ba881a0c31f35bbfe | NYFGBY 3x70 6.00 kV |  | No action |  | 0.23 | 1.0 | 0.27 | 0.103 | 0.0 | 1.0 | 1.0 | 0.0
294 | e5e5647e295844fb815774acf5145bf8 | NYFGBY 3x95 6.00 kV |  | No action |  | 0.275 | 1.0 | 0.195 | 0.099 | 0.0 | 1.0 | 1.0 | 0.0
295 | 06be7d3695244876a092e5a1294f3981 | NYSEY 3x120 6.00 kV |  | No action |  | 0.284 | 1.0 | 0.153 | 0.09891 | 0.0 | 1.0 | 1.0 | 0.0
296 | 87caa2425b174c34a7a228d0afe6581b | NYSEY 3x120 10.00 kV |  | No action |  | 0.312 | 1.0 | 0.155 | 0.099 | 0.0 | 1.0 | 1.0 | 0.0
297 | a6f0a8f6fbb64622a05076941c8bf8fb | NYSEY 3x150 6.00 kV |  | No action |  | 0.322 | 1.0 | 0.124 | 0.09577 | 0.0 | 1.0 | 1.0 | 0.0
298 | 0055b21540f64605b164fbbd007150ad | NYSEY 3x150 10.00 kV |  | No action |  | 0.35 | 1.0 | 0.127 | 0.096 | 0.0 | 1.0 | 1.0 | 0.0
299 | b9879fe9539441a3986fdf7adeb94b99 | NYSEY 3x185 6.00 kV |  | No action |  | 0.368 | 1.0 | 0.0991 | 0.09294 | 0.0 | 1.0 | 1.0 | 0.0
300 | aeb972be5fff4ae1992b0ba6122f5e88 | NYSEY 3x185 10.00 kV |  | No action |  | 0.394 | 1.0 | 0.101 | 0.093 | 0.0 | 1.0 | 1.0 | 0.0
301 | 8d61e3b92c6948aa8be43dbe2e7dead6 | NYSEY 3x240 6.00 kV |  | No action |  | 0.43 | 1.0 | 0.0754 | 0.08918 | 0.0 | 1.0 | 1.0 | 0.0
302 | 58cd3e9176fe4e0f88fd49220f427785 | NYSEY 3x240 10.00 kV |  | No action |  | 0.455 | 1.0 | 0.079 | 0.089 | 0.0 | 1.0 | 1.0 | 0.0
303 | 378f96500e1d4bbb97556705fc366a97 | NYSEY 3x25 10.00 kV |  | No action |  | 0.133 | 1.0 | 0.723 | 0.127 | 0.0 | 1.0 | 1.0 | 0.0
304 | 21af8e78d74a4751a91db6ff422a92c5 | NYSEY 3x300 6.00 kV |  | No action |  | 0.49 | 1.0 | 0.0601 | 0.08698 | 0.0 | 1.0 | 1.0 | 0.0
305 | 7e98b50ab4634614be981744c6855eca | NYSEY 3x300 10.00 kV |  | No action |  | 0.512 | 1.0 | 0.064 | 0.087 | 0.0 | 1.0 | 1.0 | 0.0
306 | 2e87bba099f54a76b313c0a2681dda50 | NYSEY 3x35 6.00 kV |  | No action |  | 0.137 | 1.0 | 0.524 | 0.11995 | 0.0 | 1.0 | 1.0 | 0.0
307 | 6fa58654a2024b54b129e950ce608474 | NYSEY 3x35 10.00 kV |  | No action |  | 0.16 | 1.0 | 0.525 | 0.12 | 0.0 | 1.0 | 1.0 | 0.0
308 | eedbcc612ff641b3a8ced370f9922ac7 | NYSEY 3x50 6.00 kV |  | No action |  | 0.165 | 1.0 | 0.387 | 0.11398 | 0.0 | 1.0 | 1.0 | 0.0
309 | f3f57d795c98424dbdef257da055051b | NYSEY 3x50 10.00 kV |  | No action |  | 0.189 | 1.0 | 0.388 | 0.114 | 0.0 | 1.0 | 1.0 | 0.0
310 | 17d61806388f4d36a6d03e958919dbb6 | NYSEY 3x70 6.00 kV |  | No action |  | 0.204 | 1.0 | 0.268 | 0.10739 | 0.0 | 1.0 | 1.0 | 0.0
311 | ec530bc717634968a2afccc36db2cecd | NYSEY 3x70 10.00 kV |  | No action |  | 0.23 | 1.0 | 0.269 | 0.107 | 0.0 | 1.0 | 1.0 | 0.0
312 | da16c938b92a4f4f956fe71ab56be1d8 | NYSEY 3x95 6.00 kV |  | No action |  | 0.248 | 1.0 | 0.193 | 0.10236 | 0.0 | 1.0 | 1.0 | 0.0
313 | a7d5a346dbfd420ea86753aa36e169ed | NYSEY 3x95 10.00 kV |  | No action |  | 0.275 | 1.0 | 0.194 | 0.102 | 0.0 | 1.0 | 1.0 | 0.0
314 | 5ce8336774ec47ec8490e6c797a0f031 | NYY 3x120/70 1.00 kV |  | No action |  | 0.313 | 1.0 | 0.154 | 0.078 | 0.0 | 0.96 | 0.347 | 0.0
315 | a6d341ff14c247b7b268e34351c43150 | NYY 3x150/70 1.00 kV |  | No action |  | 0.353 | 1.0 | 0.126 | 0.077 | 0.0 | 0.939 | 0.362 | 0.0
316 | 087da850bb31439d944d9a87fc8cd375 | NYY 3x185/95 1.00 kV |  | No action |  | 0.399 | 1.0 | 0.101 | 0.077 | 0.0 | 0.683 | 0.356 | 0.0
317 | 2e0c44ee916d4675b5842f500ef939ab | NYY 3x240/120 1.00 kV |  | No action |  | 0.464 | 1.0 | 0.078 | 0.076 | 0.0 | 0.54 | 0.351 | 0.0
318 | 3469cd77d9d34fde842e9c82283e0aa2 | NYY 3x25/16 1.00 kV |  | No action |  | 0.128 | 1.0 | 0.722 | 0.084 | 0.0 | 4.144 | 0.395 | 0.0
319 | eed5c80e5ee0417fa218d7b4835746d0 | NYY 3x300/150 1.00 kV |  | No action |  | 0.524 | 1.0 | 0.063 | 0.076 | 0.0 | 0.44 | 0.35 | 0.0
320 | 61ab27b2355f4aeca3181f5f99bfa2de | NYY 3x35/16 1.00 kV |  | No action |  | 0.157 | 1.0 | 0.524 | 0.08 | 0.0 | 3.945 | 0.378 | 0.0
321 | af099b0213c94496abf3dfff4d4dc30b | NYY 3x50/25 1.00 kV |  | No action |  | 0.185 | 1.0 | 0.388 | 0.082 | 0.0 | 2.56 | 0.377 | 0.0
322 | e9ce5a9205be44e2bebe37793fd1ddd9 | NYY 3x70/35 1.00 kV |  | No action |  | 0.228 | 1.0 | 0.268 | 0.077 | 0.0 | 1.832 | 0.353 | 0.0
323 | 62e307b0ad8c40708356b1ef8de43a54 | NYY 3x95/50 1.00 kV |  | No action |  | 0.275 | 1.0 | 0.194 | 0.079 | 0.0 | 1.354 | 0.359 | 0.0
324 | 6125b7a253874fb8b4745c5103f7fb36 | NYY 4x1.5 1.00 kV |  | No action |  | 0.026 | 1.0 | 12.1 | 0.115 | 0.0 | 48.4 | 0.459 | 0.0
325 | 7166aa3275864d64bfc54ce430d14395 | NYY 4x10 1.00 kV |  | No action |  | 0.075 | 1.0 | 1.81 | 0.094 | 0.0 | 7.24 | 0.378 | 0.0
326 | c761ac31e391489aadd7bfbeafb681ff | NYY 4x120 1.00 kV |  | No action |  | 0.313 | 1.0 | 0.157 | 0.08 | 0.0 | 0.628 | 0.292 | 0.0
327 | 4520589c7c2c4ca79204719d21118fb6 | NYY 4x150 1.00 kV |  | No action |  | 0.353 | 1.0 | 0.125 | 0.08 | 0.0 | 0.5 | 0.292 | 0.0
328 | 18ee4407afd24aeca866350cd5460cd3 | NYY 4x16 1.00 kV |  | No action |  | 0.098 | 1.0 | 1.141 | 0.09 | 0.0 | 4.564 | 0.358 | 0.0
329 | d03470b0b55a4ee68fc9b210c45c5d4d | NYY 4x185 1.00 kV |  | No action |  | 0.399 | 1.0 | 0.101 | 0.08 | 0.0 | 0.404 | 0.292 | 0.0
330 | cd193c8b553d4182b246f64e63cc4dc8 | NYY 4x2.5 1.00 kV |  | No action |  | 0.034 | 1.0 | 7.28 | 0.11 | 0.0 | 29.12 | 0.441 | 0.0
331 | 869ccc1ad8044db48d6387d5447db75f | NYY 4x240 1.00 kV |  | No action |  | 0.464 | 1.0 | 0.077 | 0.079 | 0.0 | 0.308 | 0.29 | 0.0
332 | 2bc21a0dbe434a9d9a9cbe9c4e340efb | NYY 4x25 1.00 kV |  | No action |  | 0.128 | 1.0 | 0.724 | 0.086 | 0.0 | 2.896 | 0.355 | 0.0
333 | d0401de05441443fbbf75db931d4518b | NYY 4x300 1.00 kV |  | No action |  | 0.524 | 1.0 | 0.063 | 0.079 | 0.0 | 0.252 | 0.289 | 0.0
334 | 593c834e15ed4b3eadb94db850b5f442 | NYY 4x35 1.00 kV |  | No action |  | 0.157 | 1.0 | 0.526 | 0.083 | 0.0 | 2.104 | 0.314 | 0.0
335 | f187577163674e0c994d16129b2f89d6 | NYY 4x4 1.00 kV |  | No action |  | 0.044 | 1.0 | 4.56 | 0.107 | 0.0 | 18.24 | 0.426 | 0.0
336 | 3d214b56e4704f6da94d5abfa6fdee89 | NYY 4x50 1.00 kV |  | No action |  | 0.185 | 1.0 | 0.389 | 0.083 | 0.0 | 1.556 | 0.312 | 0.0
337 | ea1b7e0823cf40f5972b0d946a6df7ce | NYY 4x6 1.00 kV |  | No action |  | 0.056 | 1.0 | 3.03 | 0.1 | 0.0 | 12.12 | 0.403 | 0.0
338 | d45906af60c24d03a4b59b3d613f561b | NYY 4x70 1.00 kV |  | No action |  | 0.228 | 1.0 | 0.271 | 0.082 | 0.0 | 1.084 | 0.3 | 0.0
339 | b42e63e8d6514405a6b193038bcb96e5 | NYY 4x95 1.00 kV |  | No action |  | 0.275 | 1.0 | 0.197 | 0.082 | 0.0 | 0.788 | 0.299 | 0.0
340 | 29dd3d78e4c94001abcb660fa0630438 | PILC-AL 1x120 1.00 kV |  | No action |  | 0.305 | 1.0 | 0.253 | 0.09 | 0.0 | 1.0 | 1.0 | 0.0
341 | d509fcd4e8dc43509b400f00774a69ab | PILC-AL 1x150 1.00 kV |  | No action |  | 0.35 | 1.0 | 0.206 | 0.088 | 0.0 | 1.0 | 1.0 | 0.0
342 | 7cb163fc6b74441a88f9d50a5cd8b285 | PILC-AL 1x185 1.00 kV |  | No action |  | 0.405 | 1.0 | 0.164 | 0.086 | 0.0 | 1.0 | 1.0 | 0.0
343 | dbf899c48463471b8fb955968c434f52 | PILC-AL 1x240 1.00 kV |  | No action |  | 0.485 | 1.0 | 0.125 | 0.084 | 0.0 | 1.0 | 1.0 | 0.0
344 | 643edbe267e546a4b7dc3c1166415d2c | PILC-AL 1x300 1.00 kV |  | No action |  | 0.56 | 1.0 | 0.1 | 0.083 | 0.0 | 1.0 | 1.0 | 0.0
345 | 89f8c35f98f8435a8f62ae69af4425ea | PILC-AL 1x50 1.00 kV |  | No action |  | 0.165 | 1.0 | 0.641 | 0.107 | 0.0 | 1.0 | 1.0 | 0.0
346 | cc9f700a30474080b6192ae2d74ef6a7 | PILC-AL 1x70 1.00 kV |  | No action |  | 0.21 | 1.0 | 0.443 | 0.097 | 0.0 | 1.0 | 1.0 | 0.0
347 | a03af69468d14288b9e1f6b583e827e4 | PILC-AL 1x95 1.00 kV |  | No action |  | 0.26 | 1.0 | 0.32 | 0.093 | 0.0 | 1.0 | 1.0 | 0.0
348 | 6e925f1995744c8f817fe07d8a14c436 | PILC-AL 3x120 1.00 kV |  | No action |  | 0.255 | 1.0 | 0.253 | 0.068 | 0.0 | 1.0 | 1.0 | 0.0
349 | 6c6a78968b06406282bc7922451b7053 | PILC-AL 3x120 11.00 kV |  | No action |  | 0.22 | 1.0 | 0.253 | 0.083 | 0.0 | 1.0 | 1.0 | 0.0
350 | 356b252a941e4a458a2e8b3f3d4a8429 | PILC-AL 3x150 1.00 kV |  | No action |  | 0.29 | 1.0 | 0.206 | 0.069 | 0.0 | 1.0 | 1.0 | 0.0
351 | 1853a44163c84f079a86712c01622dee | PILC-AL 3x150 11.00 kV |  | No action |  | 0.245 | 1.0 | 0.206 | 0.082 | 0.0 | 1.0 | 1.0 | 0.0
352 | b2c6caf8ad6a4207a589ca02f21a340c | PILC-AL 3x185 1.00 kV |  | No action |  | 0.335 | 1.0 | 0.164 | 0.068 | 0.0 | 1.0 | 1.0 | 0.0
353 | b520660612234eeea35fda517e1344aa | PILC-AL 3x185 11.00 kV |  | No action |  | 0.28 | 1.0 | 0.164 | 0.08 | 0.0 | 1.0 | 1.0 | 0.0
354 | 589d23bdabc84da0b2de4fb724a15330 | PILC-AL 3x240 1.00 kV |  | No action |  | 0.4 | 1.0 | 0.125 | 0.068 | 0.0 | 1.0 | 1.0 | 0.0
355 | 8745aeecee51452b85c7bb6a3ca023d6 | PILC-AL 3x240 11.00 kV |  | No action |  | 0.325 | 1.0 | 0.125 | 0.078 | 0.0 | 1.0 | 1.0 | 0.0
356 | 1d5c6955506c4a9faf0e9a02be15df95 | PILC-AL 3x25 1.00 kV |  | No action |  | 0.093 | 1.0 | 1.2 | 0.076 | 0.0 | 1.0 | 1.0 | 0.0
357 | a9937a11ac0b4feeac8222a2def5c9d9 | PILC-AL 3x25 11.00 kV |  | No action |  | 0.089 | 1.0 | 1.2 | 0.105 | 0.0 | 1.0 | 1.0 | 0.0
358 | 98cde4c1123b468c8199090da630e2c8 | PILC-AL 3x300 1.00 kV |  | No action |  | 0.46 | 1.0 | 0.1 | 0.067 | 0.0 | 1.0 | 1.0 | 0.0
359 | 263e52108abf47768e1b242ae3a39ce1 | PILC-AL 3x300 11.00 kV |  | No action |  | 0.365 | 1.0 | 0.1 | 0.076 | 0.0 | 1.0 | 1.0 | 0.0
360 | 668f48fab797401dbb6e83fe9260b891 | PILC-AL 3x35 1.00 kV |  | No action |  | 0.115 | 1.0 | 0.868 | 0.074 | 0.0 | 1.0 | 1.0 | 0.0
361 | b90266a9a7a8461f8961ab6307363519 | PILC-AL 3x35 11.00 kV |  | No action |  | 0.11 | 1.0 | 0.868 | 0.098 | 0.0 | 1.0 | 1.0 | 0.0
362 | 8673d0a1972e407c8ff0180a3a281236 | PILC-AL 3x50 1.00 kV |  | No action |  | 0.14 | 1.0 | 0.641 | 0.083 | 0.0 | 1.0 | 1.0 | 0.0
363 | 90060d01cb7341c4afe5a25df12bce5d | PILC-AL 3x50 11.00 kV |  | No action |  | 0.13 | 1.0 | 0.641 | 0.094 | 0.0 | 1.0 | 1.0 | 0.0
364 | fb02153530154c03849aab44786f38e8 | PILC-AL 3x70 1.00 kV |  | No action |  | 0.175 | 1.0 | 0.443 | 0.071 | 0.0 | 1.0 | 1.0 | 0.0
365 | 6b09c193a2b445ba8ccd40e3188afda1 | PILC-AL 3x70 11.00 kV |  | No action |  | 0.16 | 1.0 | 0.443 | 0.09 | 0.0 | 1.0 | 1.0 | 0.0
366 | d7a48d0c38404ded953609109315e344 | PILC-AL 3x95 1.00 kV |  | No action |  | 0.22 | 1.0 | 0.32 | 0.069 | 0.0 | 1.0 | 1.0 | 0.0
367 | 0c3bfb87b41643ad9e8920b6016291b4 | PILC-AL 3x95 11.00 kV |  | No action |  | 0.19 | 1.0 | 0.32 | 0.086 | 0.0 | 1.0 | 1.0 | 0.0
368 | b23234ddbb0c4effb4384b0b25ba4eaf | PILC-CU 1x120 1.00 kV |  | No action |  | 0.305 | 1.0 | 0.153 | 0.09 | 0.0 | 1.0 | 1.0 | 0.0
369 | 40c788e156f54512817ffa26e45fad19 | PILC-CU 1x150 1.00 kV |  | No action |  | 0.35 | 1.0 | 0.124 | 0.088 | 0.0 | 1.0 | 1.0 | 0.0
370 | 5c1c7e70ca1b47b2adbc7b72a56528a8 | PILC-CU 1x185 1.00 kV |  | No action |  | 0.405 | 1.0 | 0.0991 | 0.086 | 0.0 | 1.0 | 1.0 | 0.0
371 | 72b55822e7084a968c46f1c4bf93531c | PILC-CU 1x240 1.00 kV |  | No action |  | 0.485 | 1.0 | 0.0754 | 0.084 | 0.0 | 1.0 | 1.0 | 0.0
372 | a0be9f9e7ec747d5bbb15700341f38d4 | PILC-CU 1x300 1.00 kV |  | No action |  | 0.56 | 1.0 | 0.0601 | 0.083 | 0.0 | 1.0 | 1.0 | 0.0
373 | b2619ca8e0aa4dc485bc138a4ef5a248 | PILC-CU 1x400 1.00 kV |  | No action |  | 0.65 | 1.0 | 0.047 | 0.081 | 0.0 | 1.0 | 1.0 | 0.0
374 | c1c656f363e54cf8b6541001c7666288 | PILC-CU 1x50 1.00 kV |  | No action |  | 0.165 | 1.0 | 0.387 | 0.102 | 0.0 | 1.0 | 1.0 | 0.0
375 | 1b58d9134bc045e2a8eef2fbc97bd0f6 | PILC-CU 1x70 1.00 kV |  | No action |  | 0.21 | 1.0 | 0.268 | 0.097 | 0.0 | 1.0 | 1.0 | 0.0
376 | acc9cf5788ce498da567e83025dcc440 | PILC-CU 1x95 1.00 kV |  | No action |  | 0.26 | 1.0 | 0.193 | 0.093 | 0.0 | 1.0 | 1.0 | 0.0
377 | fa3c50f952a3479992863d6c554e32aa | PILC-CU 3x120 1.00 kV |  | No action |  | 0.325 | 1.0 | 0.153 | 0.068 | 0.0 | 1.0 | 1.0 | 0.0
378 | 2412ce2a7e42460780fa39ca621864bb | PILC-CU 3x120 11.00 kV |  | No action |  | 0.28 | 1.0 | 0.153 | 0.083 | 0.0 | 1.0 | 1.0 | 0.0
379 | 445ba45f65cb4f5fa2442b06e52405f3 | PILC-CU 3x150 1.00 kV |  | No action |  | 0.375 | 1.0 | 0.124 | 0.069 | 0.0 | 1.0 | 1.0 | 0.0
380 | 1705266ffbf143e4bd94f372602841b8 | PILC-CU 3x150 11.00 kV |  | No action |  | 0.315 | 1.0 | 0.124 | 0.082 | 0.0 | 1.0 | 1.0 | 0.0
381 | 6669dd95f65948a9be46f6f927112725 | PILC-CU 3x185 1.00 kV |  | No action |  | 0.43 | 1.0 | 0.0991 | 0.068 | 0.0 | 1.0 | 1.0 | 0.0
382 | a378ec8133a148458701b0c159add8d7 | PILC-CU 3x185 11.00 kV |  | No action |  | 0.355 | 1.0 | 0.0991 | 0.08 | 0.0 | 1.0 | 1.0 | 0.0
383 | fbc21c4388c146fdb32d7d60b3a01f03 | PILC-CU 3x240 1.00 kV |  | No action |  | 0.51 | 1.0 | 0.0754 | 0.068 | 0.0 | 1.0 | 1.0 | 0.0
384 | 760a5a45f1ed48fd9cfbb11254236ccc | PILC-CU 3x240 11.00 kV |  | No action |  | 0.41 | 1.0 | 0.0754 | 0.078 | 0.0 | 1.0 | 1.0 | 0.0
385 | cfb098e809e54f17a4fead944fb8e920 | PILC-CU 3x25 1.00 kV |  | No action |  | 0.12 | 1.0 | 0.727 | 0.076 | 0.0 | 1.0 | 1.0 | 0.0
386 | 225006b051ef40ddb6a815738fbea0ce | PILC-CU 3x25 11.00 kV |  | No action |  | 0.115 | 1.0 | 0.727 | 0.105 | 0.0 | 1.0 | 1.0 | 0.0
387 | 68a276ac830440fe8615cae6425f370b | PILC-CU 3x300 1.00 kV |  | No action |  | 0.59 | 1.0 | 0.0601 | 0.067 | 0.0 | 1.0 | 1.0 | 0.0
388 | 657f4f0e855845ada266ac66525f0ae2 | PILC-CU 3x300 11.00 kV |  | No action |  | 0.46 | 1.0 | 0.0601 | 0.076 | 0.0 | 1.0 | 1.0 | 0.0
389 | 740e2be23fdb4408ab90cc95851e643a | PILC-CU 3x35 1.00 kV |  | No action |  | 0.15 | 1.0 | 0.524 | 0.074 | 0.0 | 1.0 | 1.0 | 0.0
390 | 5a8ee3a61f7b45899ee9c137bd678e54 | PILC-CU 3x35 11.00 kV |  | No action |  | 0.14 | 1.0 | 0.524 | 0.098 | 0.0 | 1.0 | 1.0 | 0.0
391 | 9fa9a1d111a945c2a288f009ce198814 | PILC-CU 3x400 1.00 kV |  | No action |  | 0.68 | 1.0 | 0.047 | 0.067 | 0.0 | 1.0 | 1.0 | 0.0
392 | 3ba579d7126648ecbf7740bcdb1bb92e | PILC-CU 3x400 11.00 kV |  | No action |  | 0.52 | 1.0 | 0.047 | 0.075 | 0.0 | 1.0 | 1.0 | 0.0
393 | 1b0c9ed3d8ff4b64b38decb96ce2d623 | PILC-CU 3x50 1.00 kV |  | No action |  | 0.18 | 1.0 | 0.387 | 0.073 | 0.0 | 1.0 | 1.0 | 0.0
394 | 01f9588dc5ce45449c4e44c33941634f | PILC-CU 3x50 11.00 kV |  | No action |  | 0.165 | 1.0 | 0.387 | 0.094 | 0.0 | 1.0 | 1.0 | 0.0
395 | b8fea1cda66c4538ab9995f1f8da0268 | PILC-CU 3x70 1.00 kV |  | No action |  | 0.23 | 1.0 | 0.268 | 0.071 | 0.0 | 1.0 | 1.0 | 0.0
396 | 949fc3dcf3734437a1033ba7388ca52f | PILC-CU 3x70 11.00 kV |  | No action |  | 0.205 | 1.0 | 0.268 | 0.09 | 0.0 | 1.0 | 1.0 | 0.0
397 | 818a98be914644809a0cd2cd2e1be648 | PILC-CU 3x95 1.00 kV |  | No action |  | 0.28 | 1.0 | 0.193 | 0.069 | 0.0 | 1.0 | 1.0 | 0.0
398 | 1dcd05b598f34791965aefe8ea59a91c | PILC-CU 3x95 11.00 kV |  | No action |  | 0.245 | 1.0 | 0.193 | 0.086 | 0.0 | 1.0 | 1.0 | 0.0
399 | 391b85ca89184b8cb316ccc689f848ab | PVC-SWA-AL 2x16 1.00 kV |  | No action |  | 0.071 | 1.0 | 1.89 | 0.086 | 0.0 | 1.0 | 1.0 | 0.0
400 | d5882dc265714f15b61e7a99aac5ee6b | PVC-SWA-AL 2x25 1.00 kV |  | No action |  | 0.094 | 1.0 | 1.2 | 0.085 | 0.0 | 1.0 | 1.0 | 0.0
401 | b0c33520b1a345499947813ea4a84f58 | PVC-SWA-AL 2x35 1.00 kV |  | No action |  | 0.115 | 1.0 | 0.868 | 0.082 | 0.0 | 1.0 | 1.0 | 0.0
402 | 6d11106e3cb6406bb87e5b5d739b02e9 | PVC-SWA-AL 2x50 1.00 kV |  | No action |  | 0.139 | 1.0 | 0.641 | 0.082 | 0.0 | 1.0 | 1.0 | 0.0
403 | dfb023cded4147a09500dc7caf807a1b | PVC-SWA-AL 2x70 1.00 kV |  | No action |  | 0.175 | 1.0 | 0.443 | 0.079 | 0.0 | 1.0 | 1.0 | 0.0
404 | 6e4ee6b4eabb4764b1a48593f2e05bb4 | PVC-SWA-AL 2x95 1.00 kV |  | No action |  | 0.211 | 1.0 | 0.32 | 0.078 | 0.0 | 1.0 | 1.0 | 0.0
405 | 9af76e5df8d54e669b2fe92b5daeaf7b | PVC-SWA-AL 3x120 1.00 kV |  | No action |  | 0.216 | 1.0 | 0.253 | 0.077 | 0.0 | 1.0 | 1.0 | 0.0
406 | cc258f5490e54125b426f774593daf5f | PVC-SWA-AL 3x150 1.00 kV |  | No action |  | 0.25 | 1.0 | 0.206 | 0.077 | 0.0 | 1.0 | 1.0 | 0.0
407 | bae607f961ee4bde9dcce4fba606c73b | PVC-SWA-AL 3x16 1.00 kV |  | No action |  | 0.061 | 1.0 | 1.89 | 0.086 | 0.0 | 1.0 | 1.0 | 0.0
408 | 8dc5c9dc9cb041d792315445efc92d09 | PVC-SWA-AL 3x185 1.00 kV |  | No action |  | 0.287 | 1.0 | 0.164 | 0.077 | 0.0 | 1.0 | 1.0 | 0.0
409 | 2642442423b742c783c0e9aef5326809 | PVC-SWA-AL 3x240 1.00 kV |  | No action |  | 0.342 | 1.0 | 0.125 | 0.076 | 0.0 | 1.0 | 1.0 | 0.0
410 | 684508a9bdf84682a101fb23d1f91095 | PVC-SWA-AL 3x25 1.00 kV |  | No action |  | 0.08 | 1.0 | 1.2 | 0.085 | 0.0 | 1.0 | 1.0 | 0.0
411 | 0a6613eeacec435e8623cff7e9cbb3f3 | PVC-SWA-AL 3x300 1.00 kV |  | No action |  | 0.399 | 1.0 | 0.1 | 0.076 | 0.0 | 1.0 | 1.0 | 0.0
412 | 22770317500e4d96866812edb571c1c0 | PVC-SWA-AL 3x35 1.00 kV |  | No action |  | 0.99 | 1.0 | 0.868 | 0.082 | 0.0 | 1.0 | 1.0 | 0.0
413 | 6e2cf437d264479ba353ab5065d684da | PVC-SWA-AL 3x50 1.00 kV |  | No action |  | 0.119 | 1.0 | 0.641 | 0.082 | 0.0 | 1.0 | 1.0 | 0.0
414 | 1d5ede6b2a074d6eb1918a7d1b5a8873 | PVC-SWA-AL 3x70 1.00 kV |  | No action |  | 0.151 | 1.0 | 0.443 | 0.079 | 0.0 | 1.0 | 1.0 | 0.0
415 | 09c8caf9842d444babc584d2ce36c79b | PVC-SWA-AL 3x95 1.00 kV |  | No action |  | 0.186 | 1.0 | 0.32 | 0.078 | 0.0 | 1.0 | 1.0 | 0.0
416 | d79d17e99d2541a2bae319decbef0ebe | PVC-SWA-CU 1x120 1.00 kV |  | No action |  | 0.383 | 1.0 | 0.153 | 0.099 | 0.0 | 1.0 | 1.0 | 0.0
417 | 13448c6fb819409691151ccaed6d9e2e | PVC-SWA-CU 1x150 1.00 kV |  | No action |  | 0.436 | 1.0 | 0.124 | 0.097 | 0.0 | 1.0 | 1.0 | 0.0
418 | 418c3027bc424d059809840dcf08b166 | PVC-SWA-CU 1x185 1.00 kV |  | No action |  | 0.49 | 1.0 | 0.0991 | 0.095 | 0.0 | 1.0 | 1.0 | 0.0
419 | cb33f819cef145c589da72664e60d147 | PVC-SWA-CU 1x240 1.00 kV |  | No action |  | 0.566 | 1.0 | 0.0754 | 0.093 | 0.0 | 1.0 | 1.0 | 0.0
420 | cec26ec95c114933a8275ef7a0a22733 | PVC-SWA-CU 1x300 1.00 kV |  | No action |  | 0.616 | 1.0 | 0.0601 | 0.091 | 0.0 | 1.0 | 1.0 | 0.0
421 | 1f98916b058d4333ac1f466ad2a36102 | PVC-SWA-CU 1x400 1.00 kV |  | No action |  | 0.674 | 1.0 | 0.047 | 0.091 | 0.0 | 1.0 | 1.0 | 0.0
422 | c86cabed997147c7b2cea6bb9392c238 | PVC-SWA-CU 1x50 1.00 kV |  | No action |  | 0.23 | 1.0 | 0.387 | 0.109 | 0.0 | 1.0 | 1.0 | 0.0
423 | 8b1f78cf4187422bbcdd32d01c842e6f | PVC-SWA-CU 1x70 1.00 kV |  | No action |  | 0.286 | 1.0 | 0.268 | 0.104 | 0.0 | 1.0 | 1.0 | 0.0
424 | f88dfdcdc6b0423da7d7478c20484c51 | PVC-SWA-CU 1x95 1.00 kV |  | No action |  | 0.338 | 1.0 | 0.0193 | 0.1 | 0.0 | 1.0 | 1.0 | 0.0
425 | e9a6b9ae45d0450c83549d59824cb241 | PVC-SWA-CU 2x120 1.00 kV |  | No action |  | 0.335 | 1.0 | 0.153 | 0.076 | 0.0 | 1.0 | 1.0 | 0.0
426 | bbb6ba5a822b4c39bab07f428a2713a1 | PVC-SWA-CU 2x150 1.00 kV |  | No action |  | 0.38 | 1.0 | 0.124 | 0.076 | 0.0 | 1.0 | 1.0 | 0.0
427 | 59ab9cdc1ea24f05b33e8b46e54418bc | PVC-SWA-CU 2x16 1.00 kV |  | No action |  | 0.097 | 1.0 | 1.15 | 0.088 | 0.0 | 1.0 | 1.0 | 0.0
428 | ce1a5afaa2494c5bb731089b3554a292 | PVC-SWA-CU 2x185 1.00 kV |  | No action |  | 0.44 | 1.0 | 0.0991 | 0.076 | 0.0 | 1.0 | 1.0 | 0.0
429 | 781666bf8d4c44bca38aa0e30d93a00b | PVC-SWA-CU 2x240 1.00 kV |  | No action |  | 0.52 | 1.0 | 0.0754 | 0.075 | 0.0 | 1.0 | 1.0 | 0.0
430 | 91b7a70249d54458bbc59034eef2b4d5 | PVC-SWA-CU 2x25 1.00 kV |  | No action |  | 0.13 | 1.0 | 0.727 | 0.083 | 0.0 | 1.0 | 1.0 | 0.0
431 | ec503b27480049419087ab46c1284d4b | PVC-SWA-CU 2x300 1.00 kV |  | No action |  | 0.59 | 1.0 | 0.0601 | 0.075 | 0.0 | 1.0 | 1.0 | 0.0
432 | e26086d2732d459b950e9b257224064d | PVC-SWA-CU 2x35 1.00 kV |  | No action |  | 0.16 | 1.0 | 0.524 | 0.081 | 0.0 | 1.0 | 1.0 | 0.0
433 | 62e335e26b964a6ea822178724491276 | PVC-SWA-CU 2x400 1.00 kV |  | No action |  | 0.67 | 1.0 | 0.047 | 0.074 | 0.0 | 1.0 | 1.0 | 0.0
434 | 2d0afb7640bc474b84cb872c12eae7d8 | PVC-SWA-CU 2x50 1.00 kV |  | No action |  | 0.19 | 1.0 | 0.387 | 0.081 | 0.0 | 1.0 | 1.0 | 0.0
435 | e41299ca55b24c07bed3beaa4c6039c6 | PVC-SWA-CU 2x70 1.00 kV |  | No action |  | 0.235 | 1.0 | 0.268 | 0.079 | 0.0 | 1.0 | 1.0 | 0.0
436 | 84533c8ff2e24848b1acea6e6b7268f4 | PVC-SWA-CU 2x95 1.00 kV |  | No action |  | 0.29 | 1.0 | 0.193 | 0.077 | 0.0 | 1.0 | 1.0 | 0.0
437 | a46f5360be38431eb5146f9670afbaf7 | PVC-SWA-CU 3x120 1.00 kV |  | No action |  | 0.29 | 1.0 | 0.153 | 0.076 | 0.0 | 1.0 | 1.0 | 0.0
438 | 36daea61ef494187b82cab3aa92cafd0 | PVC-SWA-CU 3x150 1.00 kV |  | No action |  | 0.335 | 1.0 | 0.124 | 0.076 | 0.0 | 1.0 | 1.0 | 0.0
439 | 799bdee501c04aec976343fbb28940d4 | PVC-SWA-CU 3x16 1.00 kV |  | No action |  | 0.083 | 1.0 | 1.15 | 0.088 | 0.0 | 1.0 | 1.0 | 0.0
440 | f7e893de57d44a798ca7377e19a7a1d0 | PVC-SWA-CU 3x185 1.00 kV |  | No action |  | 0.38 | 1.0 | 0.0991 | 0.076 | 0.0 | 1.0 | 1.0 | 0.0
441 | d02f35d215cd498db3b3dcdf17439206 | PVC-SWA-CU 3x240 1.00 kV |  | No action |  | 0.45 | 1.0 | 0.0754 | 0.075 | 0.0 | 1.0 | 1.0 | 0.0
442 | 3911fe1fa5bc49fa9274ef2aa7674411 | PVC-SWA-CU 3x25 1.00 kV |  | No action |  | 0.11 | 1.0 | 0.727 | 0.083 | 0.0 | 1.0 | 1.0 | 0.0
443 | 65092cce64ec417eb08fd6d4e37ce21e | PVC-SWA-CU 3x300 1.00 kV |  | No action |  | 0.51 | 1.0 | 0.0601 | 0.075 | 0.0 | 1.0 | 1.0 | 0.0
444 | 31ab0e367ee6417abd486fd8dcf88b72 | PVC-SWA-CU 3x35 1.00 kV |  | No action |  | 0.135 | 1.0 | 0.524 | 0.081 | 0.0 | 1.0 | 1.0 | 0.0
445 | 3c1033e1112d4bb180b8edfd04cf8db7 | PVC-SWA-CU 3x400 1.00 kV |  | No action |  | 0.59 | 1.0 | 0.047 | 0.074 | 0.0 | 1.0 | 1.0 | 0.0
446 | 86d8beb808df46558ba94eabe41803be | PVC-SWA-CU 3x50 1.00 kV |  | No action |  | 0.165 | 1.0 | 0.387 | 0.081 | 0.0 | 1.0 | 1.0 | 0.0
447 | 962ba28f78f94867b975742287779d66 | PVC-SWA-CU 3x70 1.00 kV |  | No action |  | 0.205 | 1.0 | 0.268 | 0.079 | 0.0 | 1.0 | 1.0 | 0.0
448 | 57f1f0e2aaee423bb6de91fc9ff05656 | PVC-SWA-CU 3x95 1.00 kV |  | No action |  | 0.25 | 1.0 | 0.193 | 0.077 | 0.0 | 1.0 | 1.0 | 0.0
449 | 6fd56def3c324dc4842b6e3a5ace664a | XHIV 1x185 20.00 kV |  | No action |  | 0.4 | 1.0 | 0.1 | 0.12085 | 0.0 | 1.0 | 1.0 | 0.0
450 | 8bc312da1d3d48ec9ae22cefb6522436 | XLPE-CU 3x120 11.00 kV |  | No action |  | 0.335 | 1.0 | 0.153 | 0.097 | 0.0 | 1.0 | 1.0 | 0.0
451 | c86b94aeb2cb4e95bf14db1ab0fcb114 | XLPE-CU 3x150 11.00 kV |  | No action |  | 0.375 | 1.0 | 0.124 | 0.094 | 0.0 | 1.0 | 1.0 | 0.0
452 | f53bac328395465b841477602c17dedd | XLPE-CU 3x185 11.00 kV |  | No action |  | 0.42 | 1.0 | 0.0991 | 0.092 | 0.0 | 1.0 | 1.0 | 0.0
453 | 83f16e5752cc4c91a1274c4072bb93c0 | XLPE-CU 3x240 11.00 kV |  | No action |  | 0.485 | 1.0 | 0.0754 | 0.089 | 0.0 | 1.0 | 1.0 | 0.0
454 | cb22f036e4704bcda0c1218f1dd40dc1 | XLPE-CU 3x25 11.00 kV |  | No action |  | 0.145 | 1.0 | 0.727 | 0.124 | 0.0 | 1.0 | 1.0 | 0.0
455 | 46d216bc63fc42878441ddbf133abec8 | XLPE-CU 3x300 11.00 kV |  | No action |  | 0.54 | 1.0 | 0.0601 | 0.086 | 0.0 | 1.0 | 1.0 | 0.0
456 | 93b74eb0d5514f89a84946a0734d96f0 | XLPE-CU 3x35 11.00 kV |  | No action |  | 0.17 | 1.0 | 0.524 | 0.116 | 0.0 | 1.0 | 1.0 | 0.0
457 | 6d198d3e4ada40998bfd34e3574fd2c2 | XLPE-CU 3x50 11.00 kV |  | No action |  | 0.205 | 1.0 | 0.387 | 0.111 | 0.0 | 1.0 | 1.0 | 0.0
458 | 739b945ccf8442deacf4309f8640411d | XLPE-CU 3x70 11.00 kV |  | No action |  | 0.245 | 1.0 | 0.268 | 0.106 | 0.0 | 1.0 | 1.0 | 0.0
459 | 4949835665f7450c967137beaf7dc26d | XLPE-CU 3x95 11.00 kV |  | No action |  | 0.295 | 1.0 | 0.193 | 0.1 | 0.0 | 1.0 | 1.0 | 0.0
460 | 176160d301dd4020ae0799c2df0774eb | ZEBRA 1x300 150.00 kV |  | No action |  | 0.5 | 1.0 | 0.06079 | 0.4178 | 0.0 | 1.0 | 1.0 | 0.0

## sequence_line_types
idtag | name | code | action | comment | Imax | Vnom | R | X | B | R0 | X0 | B0 | Cnf | Cnf0 | use_conductance

## transformer_types
| idtag | name | code | action | comment | HV | LV | Sn | Pcu | Pfe | I0 | Vsc | tc_type | total_positions | dV | neutral_position | asymmetry_angle | tap_module_min | tap_module_max | tap_phase_min | tap_phase_max
0 | cf3de4a4b95d49e4a9ab89f70c1873fa | 2.5 MVA 10/0.4 kV Yyn6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 2.5 | 19.0 | 3.3 | 0.13201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
1 | aae4b74094274b6aa9d85151e3d20388 | 2.5 MVA 10/0.4 kV Yyn6 ASEA |  | No action |  | 10.0 | 0.4 | 2.5 | 19.0 | 4.3 | 0.17201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
2 | a71418defbd44db8bca5e724cfbee73b | 2.5 MVA 10/0.4 kV Yyn0 wnr ASEA |  | No action |  | 10.0 | 0.4 | 2.5 | 19.0 | 3.3 | 0.13201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
3 | d285361400a94f6baea728d7728a7c18 | 2.5 MVA 10/0.4 kV Yyn0 ASEA |  | No action |  | 10.0 | 0.4 | 2.5 | 19.0 | 4.3 | 0.17201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
4 | 8e827d62396a4752a560cae0f33c93a0 | 2.5 MVA 10/0.4 kV Trafo Union wnr |  | No action |  | 10.0 | 0.4 | 2.5 | 18.0 | 3.2 | 0.128 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
5 | 18b0d8cc4fd443bfb441831e4d6d86fb | 2.5 MVA 10/0.4 kV Trafo Union |  | No action |  | 10.0 | 0.4 | 2.5 | 17.5 | 3.75 | 0.15 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
6 | b22a2f9777f4410d8ceb82a05d394767 | 2.5 MVA 10/0.4 kV Dyn7 wnr ASEA |  | No action |  | 10.0 | 0.4 | 2.5 | 19.0 | 3.3 | 0.13201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
7 | 17e816f3ff9f4dce9fc70e91f74883b8 | 2.5 MVA 10/0.4 kV Dyn7 ASEA |  | No action |  | 10.0 | 0.4 | 2.5 | 19.0 | 4.3 | 0.17201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
8 | 91c0b8f4f38c40028e55832e437e2cb2 | 2.5 MVA 10/0.4 kV Dyn5 wnr ASEA |  | No action |  | 10.0 | 0.4 | 2.5 | 19.0 | 3.3 | 0.13201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
9 | 5d7f889570b942e48568278f42e1c90f | 2.5 MVA 10/0.4 kV Dyn5 ASEA |  | No action |  | 10.0 | 0.4 | 2.5 | 19.0 | 4.3 | 0.17201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
10 | 8ffaddfe51364c05a6bd13996929e3cf | 2.5 MVA 10/0.4 kV Dyn11 wnr ASEA |  | No action |  | 10.0 | 0.4 | 2.5 | 19.0 | 3.3 | 0.13201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
11 | 385cdf9b37084d15980975ca589b7a03 | 2.5 MVA 10/0.4 kV Dyn11 ASEA |  | No action |  | 10.0 | 0.4 | 2.5 | 19.0 | 4.3 | 0.17201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
12 | 89c52c25f617447b8fd2bfb4bb1ef253 | 2.5 MVA 10/0.4 kV Dyn1 wnr ASEA |  | No action |  | 10.0 | 0.4 | 2.5 | 19.0 | 3.3 | 0.13201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
13 | 39f838c72d8d4bcc88883711b8500ac9 | 2.5 MVA 10/0.4 kV Dyn1 ASEA |  | No action |  | 10.0 | 0.4 | 2.5 | 19.0 | 4.3 | 0.17201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
14 | bda32ed6c6c24adda1e1cecdb62f06cd | 2.5 MVA 10/0.4 kV DTTHL SGB |  | No action |  | 10.0 | 0.4 | 2.5 | 18.0 | 3.15 | 0.12601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
15 | 5e4e949ddf8142f1bdf7034fc2b96859 | 2.5 MVA 10/0.4 kV DTTHIL SGB |  | No action |  | 10.0 | 0.4 | 2.5 | 13.9 | 3.35 | 0.13401 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
16 | 9b81fdd100464de0b910ad98197d3b13 | 2.5 MVA 10/0.4 kV DTTH SGB |  | No action |  | 10.0 | 0.4 | 2.5 | 18.5 | 4.2 | 0.16801 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
17 | e7fc242500f044749da873d94fef41e2 | 2.5 MVA 10/0.4 kV DOTEL 2500/10 SGB |  | No action |  | 10.0 | 0.4 | 2.5 | 25.0 | 2.5 | 0.10001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
18 | f39951d8a7e841588e3c4dd9c4a5a9f4 | 2.5 MVA 10/0.4 kV DOTE 2500/10 SGB |  | No action |  | 10.0 | 0.4 | 2.5 | 25.0 | 3.5 | 0.14001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
19 | 4ef8f491430c45edb2388258bb382020 | 2.5 MVA 10/0.4 kV 4.8 GEAFOL |  | No action |  | 10.0 | 0.4 | 2.5 | 15.5 | 4.8 | 0.192 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
20 | f4ab1af8a195436296493ad23176ef56 | 2.5 MVA 10/0.4 kV 3.3 GEAFOL |  | No action |  | 10.0 | 0.4 | 2.5 | 19.0 | 3.3 | 0.132 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
21 | e320bfd2800c48d7b2dba817f0878a6a | 2 MVA 10/0.4 kV Yyn6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 2.0 | 15.5 | 2.75 | 0.13751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
22 | 612358126507429aa26d8b6f4917a1e5 | 2 MVA 10/0.4 kV Yyn6 ASEA |  | No action |  | 10.0 | 0.4 | 2.0 | 15.5 | 3.5 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
23 | 389927e92626479995ea7424cb473621 | 2 MVA 10/0.4 kV Yyn0 wnr ASEA |  | No action |  | 10.0 | 0.4 | 2.0 | 15.5 | 2.75 | 0.13751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
24 | 2a19b9e0162f46ba8c3d96538201bdaa | 2 MVA 10/0.4 kV Yyn0 ASEA |  | No action |  | 10.0 | 0.4 | 2.0 | 15.5 | 3.5 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
25 | 439d7fa071d242d189e608a55f142117 | 2 MVA 10/0.4 kV Trafo Union wnr |  | No action |  | 10.0 | 0.4 | 2.0 | 15.5 | 2.95 | 0.1475 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
26 | fadb2d2c5fbd41198f2dd6cc7bca82c9 | 2 MVA 10/0.4 kV Trafo Union |  | No action |  | 10.0 | 0.4 | 2.0 | 15.0 | 3.45 | 0.1725 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
27 | c4bed3e043924d798338c39423281190 | 2 MVA 10/0.4 kV Dyn7 wnr ASEA |  | No action |  | 10.0 | 0.4 | 2.0 | 15.5 | 2.75 | 0.13751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
28 | 8555cab87504420abc9b212425a1f415 | 2 MVA 10/0.4 kV Dyn7 ASEA |  | No action |  | 10.0 | 0.4 | 2.0 | 15.5 | 3.5 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
29 | fe39e7605e564b7b993fb33ca10937b2 | 2 MVA 10/0.4 kV Dyn5 wnr ASEA |  | No action |  | 10.0 | 0.4 | 2.0 | 15.5 | 2.75 | 0.13751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
30 | 1df46bf33a35473fae7fcbec0516400e | 2 MVA 10/0.4 kV Dyn5 ASEA |  | No action |  | 10.0 | 0.4 | 2.0 | 15.5 | 3.5 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
31 | 8489d4fa284b44819065b0edd4e4ccdd | 2 MVA 10/0.4 kV Dyn11 wnr ASEA |  | No action |  | 10.0 | 0.4 | 2.0 | 15.5 | 2.75 | 0.13751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
32 | 90cede6b8ca04e38b40a2e44f401129b | 2 MVA 10/0.4 kV Dyn11 ASEA |  | No action |  | 10.0 | 0.4 | 2.0 | 15.5 | 3.5 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
33 | 8edad214172a47539c86d1d9d5cfdca1 | 2 MVA 10/0.4 kV Dyn1 wnr ASEA |  | No action |  | 10.0 | 0.4 | 2.0 | 15.5 | 2.75 | 0.13751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
34 | b3a6743722704cb0b7cb8ca799e4bdb8 | 2 MVA 10/0.4 kV Dyn1 ASEA |  | No action |  | 10.0 | 0.4 | 2.0 | 15.5 | 3.5 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
35 | 7e94e1bab96f42f791c4a4e011867edb | 2 MVA 10/0.4 kV DTTHL SGB |  | No action |  | 10.0 | 0.4 | 2.0 | 15.3 | 2.7 | 0.13501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
36 | 21cd5b0f538149248e15616209649353 | 2 MVA 10/0.4 kV DTTHIL SGB |  | No action |  | 10.0 | 0.4 | 2.0 | 12.0 | 2.85 | 0.14251 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
37 | 1f072de2279349bdae66223d9ad926c5 | 2 MVA 10/0.4 kV DTTH SGB |  | No action |  | 10.0 | 0.4 | 2.0 | 16.7 | 3.5 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
38 | 25884fa67ab94f04ab2c0b291e1b7198 | 2 MVA 10/0.4 kV DOTEL 2000/10 SGB |  | No action |  | 10.0 | 0.4 | 2.0 | 21.5 | 2.1 | 0.10501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
39 | ff06f80e85d64b62ba1feb5058874278 | 2 MVA 10/0.4 kV DOTE 2000/10 SGB |  | No action |  | 10.0 | 0.4 | 2.0 | 21.5 | 2.9 | 0.14501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
40 | d832d935d43a433988adc8ce094ed6e0 | 2 MVA 10/0.4 kV 3.9 GEAFOL |  | No action |  | 10.0 | 0.4 | 2.0 | 12.7 | 3.9 | 0.195 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
41 | 748e5bcce0bb4440be4b08797aef334c | 2 MVA 10/0.4 kV 2.8 GEAFOL |  | No action |  | 10.0 | 0.4 | 2.0 | 13.0 | 2.8 | 0.14 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
42 | 4e9edca235594142913a5f222839420c | 1.6 MVA 10/0.4 kV Yyn6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 1.6 | 12.7 | 2.2 | 0.13751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
43 | 683d9f5550d64d01ac221a97720cf17c | 1.6 MVA 10/0.4 kV Yyn6 ASEA |  | No action |  | 10.0 | 0.4 | 1.6 | 12.7 | 2.8 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
44 | 401cfb3775094b9abf6e864861f23153 | 1.6 MVA 10/0.4 kV Yyn0 wnr ASEA |  | No action |  | 10.0 | 0.4 | 1.6 | 12.7 | 2.2 | 0.13751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
45 | e7771d9536db4ac1998de39fd26c90f4 | 1.6 MVA 10/0.4 kV Yyn0 ASEA |  | No action |  | 10.0 | 0.4 | 1.6 | 12.7 | 2.8 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
46 | ad321c6f09e64a80b21ab132dc8c4848 | 1.6 MVA 10/0.4 kV Trafo Union wnr |  | No action |  | 10.0 | 0.4 | 1.6 | 13.0 | 2.2 | 0.1375 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
47 | 51e96ac48e5b435fac7116756e1b9bae | 1.6 MVA 10/0.4 kV Trafo Union |  | No action |  | 10.0 | 0.4 | 1.6 | 12.5 | 2.7 | 0.16875 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
48 | 2d1f7d4c01884c18965a81f2a4168810 | 1.6 MVA 10/0.4 kV Dyn7 wnr ASEA |  | No action |  | 10.0 | 0.4 | 1.6 | 12.7 | 2.2 | 0.13751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
49 | 9ac3538f44cd4f23ab1b8f98103b7298 | 1.6 MVA 10/0.4 kV Dyn7 ASEA |  | No action |  | 10.0 | 0.4 | 1.6 | 12.7 | 2.8 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
50 | b615517de9f74e8d955b3f3ed87fd54e | 1.6 MVA 10/0.4 kV Dyn5 wnr ASEA |  | No action |  | 10.0 | 0.4 | 1.6 | 12.7 | 2.2 | 0.13751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
51 | 3542d5a4ad864cbbbe8ddc949cc11354 | 1.6 MVA 10/0.4 kV Dyn5 ASEA |  | No action |  | 10.0 | 0.4 | 1.6 | 12.7 | 2.8 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
52 | 1031721ba43b4f0bb1323a58027f8675 | 1.6 MVA 10/0.4 kV Dyn11 wnr ASEA |  | No action |  | 10.0 | 0.4 | 1.6 | 12.7 | 2.2 | 0.13751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
53 | f761fa198178471bbf131b92607f0d08 | 1.6 MVA 10/0.4 kV Dyn11 ASEA |  | No action |  | 10.0 | 0.4 | 1.6 | 12.7 | 2.8 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
54 | 802742056d264fc5970a05dd61772fb8 | 1.6 MVA 10/0.4 kV Dyn1 wnr ASEA |  | No action |  | 10.0 | 0.4 | 1.6 | 12.7 | 2.2 | 0.13751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
55 | 9f679c897b4944d0958b4261ffa1c272 | 1.6 MVA 10/0.4 kV Dyn1 ASEA |  | No action |  | 10.0 | 0.4 | 1.6 | 12.7 | 2.8 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
56 | d60c9299684f4474bc504ebf21681cf6 | 1.6 MVA 10/0.4 kV DTTHL SGB |  | No action |  | 10.0 | 0.4 | 1.6 | 11.8 | 2.07 | 0.129385 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
57 | bdca2e545bf9438097acef4637dbcfe6 | 1.6 MVA 10/0.4 kV DTTHIL SGB |  | No action |  | 10.0 | 0.4 | 1.6 | 8.8 | 2.3 | 0.14376 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
58 | fead8c3a11f4448684e8e40d2b55cfed | 1.6 MVA 10/0.4 kV DTTH SGB |  | No action |  | 10.0 | 0.4 | 1.6 | 12.5 | 2.65 | 0.165635 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
59 | 4e3481a87741450192b40bba43e28918 | 1.6 MVA 10/0.4 kV DTKa SGB |  | No action |  | 10.0 | 0.4 | 1.6 | 13.0 | 2.8 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
60 | 2935976a84f44b9a955e6867ffe96890 | 1.6 MVA 10/0.4 kV DT 1600/10 F SGB |  | No action |  | 10.0 | 0.4 | 1.6 | 12.5 | 2.8 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
61 | 5c8f819027e142739c3400038720cede | 1.6 MVA 10/0.4 kV DOTEL 1600/10 SGB |  | No action |  | 10.0 | 0.4 | 1.6 | 17.0 | 1.6 | 0.10001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
62 | 855d5e8a939b49769c606094f9685653 | 1.6 MVA 10/0.4 kV DOTE 1600/10 SGB |  | No action |  | 10.0 | 0.4 | 1.6 | 17.0 | 2.2 | 0.13751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
63 | e44cc603345c4d52802ed1ff3582c850 | 1.6 MVA 10/0.4 kV 2.8 GEAFOL |  | No action |  | 10.0 | 0.4 | 1.6 | 10.5 | 2.8 | 0.175 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
64 | aee3d14690b34ad3893920e5c80bdc07 | 1.6 MVA 10/0.4 kV 2.18 GEAFOL |  | No action |  | 10.0 | 0.4 | 1.6 | 10.9 | 2.18 | 0.13625 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
65 | 52a78b58110d4cdca7a8d9400b25d74d | 1.25 MVA 10/0.4 kV Yyn6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 1.25 | 10.5 | 1.88 | 0.15041 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
66 | fda87a4aa3bf49638de6e3d340a12821 | 1.25 MVA 10/0.4 kV Yyn6 ASEA |  | No action |  | 10.0 | 0.4 | 1.25 | 10.5 | 2.4 | 0.19201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
67 | f892c0c933784268a3c7cf92ff0520e3 | 1.25 MVA 10/0.4 kV Yyn0 wnr ASEA |  | No action |  | 10.0 | 0.4 | 1.25 | 10.5 | 1.88 | 0.15041 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
68 | 05e331c3c0974298ac999bb3bef5bbc0 | 1.25 MVA 10/0.4 kV Yyn0 ASEA |  | No action |  | 10.0 | 0.4 | 1.25 | 10.5 | 2.4 | 0.19201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
69 | cfdb542093d64230bcf5e4844dd46dac | 1.25 MVA 10/0.4 kV Trafo Union wnr |  | No action |  | 10.0 | 0.4 | 1.25 | 10.7 | 1.95 | 0.156 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
70 | ebdc3b67c5714188a1910c495f60c5be | 1.25 MVA 10/0.4 kV Trafo Union |  | No action |  | 10.0 | 0.4 | 1.25 | 10.2 | 2.4 | 0.192 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
71 | 3006280b09754e6c9f09283339e5bbd1 | 1.25 MVA 10/0.4 kV Dyn7 wnr ASEA |  | No action |  | 10.0 | 0.4 | 1.25 | 10.5 | 1.88 | 0.15041 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
72 | aa7809c599424fc8be1de2738e54f9c1 | 1.25 MVA 10/0.4 kV Dyn7 ASEA |  | No action |  | 10.0 | 0.4 | 1.25 | 10.5 | 2.4 | 0.19201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
73 | 6dc844f769a44fdaa1541283ca9d2814 | 1.25 MVA 10/0.4 kV Dyn5 wnr ASEA |  | No action |  | 10.0 | 0.4 | 1.25 | 10.5 | 1.88 | 0.15041 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
74 | e2c17fbb98d84f50bb13980357bdd8b3 | 1.25 MVA 10/0.4 kV Dyn5 ASEA |  | No action |  | 10.0 | 0.4 | 1.25 | 10.5 | 2.4 | 0.19201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
75 | 7a171bbf120f4411a33ec8d47544eba7 | 1.25 MVA 10/0.4 kV Dyn11 wnr ASEA |  | No action |  | 10.0 | 0.4 | 1.25 | 10.5 | 1.88 | 0.15041 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
76 | fe81aab3ed0743ab8d6cf90b25d06adc | 1.25 MVA 10/0.4 kV Dyn11 ASEA |  | No action |  | 10.0 | 0.4 | 1.25 | 10.5 | 2.4 | 0.19201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
77 | a495a5e70b0d4e99be80ab714e4e2bd9 | 1.25 MVA 10/0.4 kV Dyn1 wnr ASEA |  | No action |  | 10.0 | 0.4 | 1.25 | 10.5 | 1.88 | 0.15041 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
78 | 1e278fe69a9245b1a8ed2438d850488c | 1.25 MVA 10/0.4 kV Dyn1 ASEA |  | No action |  | 10.0 | 0.4 | 1.25 | 10.5 | 2.4 | 0.19201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
79 | 1a0200106ac44c738a5bab091016777e | 1.25 MVA 10/0.4 kV DTTHL SGB |  | No action |  | 10.0 | 0.4 | 1.25 | 10.5 | 1.75 | 0.14001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
80 | e72a2ca51e5943aba4896f2426bfdcd0 | 1.25 MVA 10/0.4 kV DTTHIL SGB |  | No action |  | 10.0 | 0.4 | 1.25 | 7.5 | 1.9 | 0.15201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
81 | 0847e1571c6d4c938ce94504412b8c51 | 1.25 MVA 10/0.4 kV DTTH SGB |  | No action |  | 10.0 | 0.4 | 1.25 | 10.9 | 2.25 | 0.18001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
82 | 9a31960546324921a317c1158b8f76da | 1.25 MVA 10/0.4 kV DT 1250/10 F SGB |  | No action |  | 10.0 | 0.4 | 1.25 | 11.0 | 2.3 | 0.18401 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
83 | 70f36dd29e994c55aa16d19787431a71 | 1.25 MVA 10/0.4 kV DOTEL 1250/10 SGB |  | No action |  | 10.0 | 0.4 | 1.25 | 13.5 | 1.35 | 0.10801 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
84 | 7003dd0b674245948464f7f70748d62d | 1.25 MVA 10/0.4 kV DOTE 1250/10 SGB |  | No action |  | 10.0 | 0.4 | 1.25 | 13.5 | 2.0 | 0.16001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
85 | fdae32c9778c4a36a6de6157d22117c9 | 1.25 MVA 10/0.4 kV 2.4 GEAFOL/FC |  | No action |  | 10.0 | 0.4 | 1.25 | 9.5 | 2.4 | 0.192 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
86 | ce9406cb77fc4f638eadcf935d914b1a | 1.25 MVA 10/0.4 kV 2.4 GEAFOL |  | No action |  | 10.0 | 0.4 | 1.25 | 8.8 | 2.4 | 0.192 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
87 | 8c1ffc8babdb495494dff4d0c726c23e | 1.25 MVA 10/0.4 kV 1.87 GEAFOL |  | No action |  | 10.0 | 0.4 | 1.25 | 9.1 | 1.87 | 0.1496 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
88 | 94ad8ad5a90a4ababf8c62ea2365b970 | 1 MVA 10/0.4 kV Yyn6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 1.0 | 8.8 | 1.56 | 0.15601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
89 | b086b5a870214e338710a4c20a5c0029 | 1 MVA 10/0.4 kV Yyn6 ASEA |  | No action |  | 10.0 | 0.4 | 1.0 | 8.8 | 2.0 | 0.20001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
90 | 2953fdadf4664ac09d65a60a9c77127e | 1 MVA 10/0.4 kV Yyn0 wnr ASEA |  | No action |  | 10.0 | 0.4 | 1.0 | 8.8 | 1.56 | 0.15601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
91 | 90e3d9d361c54b778650f002d5dbac42 | 1 MVA 10/0.4 kV Yyn0 ASEA |  | No action |  | 10.0 | 0.4 | 1.0 | 8.8 | 2.0 | 0.20001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
92 | 31eb9da4ef004c458dc1403ea8e041af | 1 MVA 10/0.4 kV Trafo Union wnr |  | No action |  | 10.0 | 0.4 | 1.0 | 8.7 | 1.5 | 0.15 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
93 | 6950079d17394a979c525fc36e1a191a | 1 MVA 10/0.4 kV Trafo Union |  | No action |  | 10.0 | 0.4 | 1.0 | 8.3 | 1.9 | 0.19 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
94 | 3b7736fa343a4ca5955a6ce69ac46167 | 1 MVA 10/0.4 kV Dyn7 wnr ASEA |  | No action |  | 10.0 | 0.4 | 1.0 | 8.8 | 1.56 | 0.15601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
95 | 3f1d1782d8f2461db0d30ea864bf3ddd | 1 MVA 10/0.4 kV Dyn7 ASEA |  | No action |  | 10.0 | 0.4 | 1.0 | 8.8 | 2.0 | 0.20001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
96 | 4e6140ac40264319a38206cbbec38a33 | 1 MVA 10/0.4 kV Dyn5 wnr ASEA |  | No action |  | 10.0 | 0.4 | 1.0 | 8.8 | 1.56 | 0.15601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
97 | b59ecf410e484a0a84e80e1a3a528067 | 1 MVA 10/0.4 kV Dyn5 ASEA |  | No action |  | 10.0 | 0.4 | 1.0 | 8.8 | 2.0 | 0.20001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
98 | 021a9479ed0d44fabcad08cb4ba296d2 | 1 MVA 10/0.4 kV Dyn11 wnr ASEA |  | No action |  | 10.0 | 0.4 | 1.0 | 8.8 | 1.56 | 0.15601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
99 | f8d621ee5884486e8c050ea6bcc6e096 | 1 MVA 10/0.4 kV Dyn11 ASEA |  | No action |  | 10.0 | 0.4 | 1.0 | 8.8 | 2.0 | 0.20001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
100 | fd9da08a33fc4ada8b0ca77d57b7b43b | 1 MVA 10/0.4 kV Dyn1 wnr ASEA |  | No action |  | 10.0 | 0.4 | 1.0 | 8.8 | 1.56 | 0.15601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
101 | 12124a7f767e44778c247c1b10890503 | 1 MVA 10/0.4 kV Dyn1 ASEA |  | No action |  | 10.0 | 0.4 | 1.0 | 8.8 | 2.0 | 0.20001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
102 | 0193f8301db141cabb04b7873ff55d12 | 1 MVA 10/0.4 kV DTTHL SGB |  | No action |  | 10.0 | 0.4 | 1.0 | 8.2 | 1.43 | 0.14301 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
103 | 9f76b72bb88548d1a5403c6f5e3eb532 | 1 MVA 10/0.4 kV DTTHIL SGB |  | No action |  | 10.0 | 0.4 | 1.0 | 6.1 | 1.6 | 0.16001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
104 | be5ed4a8af7549e6b7ee8062b578dc3c | 1 MVA 10/0.4 kV DTTH SGB |  | No action |  | 10.0 | 0.4 | 1.0 | 8.8 | 2.05 | 0.20501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
105 | 870a4935b6f542b094dd0b6775648154 | 1 MVA 10/0.4 kV DTKa SGB |  | No action |  | 10.0 | 0.4 | 1.0 | 8.7 | 2.1 | 0.21001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
106 | b5d410233b25437e9a3d40bfd0ef6f70 | 1 MVA 10/0.4 kV DT 1000/10 F SGB |  | No action |  | 10.0 | 0.4 | 1.0 | 9.5 | 2.0 | 0.20001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
107 | 1aa61dc3c6ac44939ab72ce76fb26c31 | 1 MVA 10/0.4 kV DT 1000 SGB |  | No action |  | 10.0 | 0.4 | 1.0 | 8.2 | 1.7 | 0.17001 | 5.5 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
108 | b6ba2ccb415042b2abbcb8c8da35c741 | 1 MVA 10/0.4 kV DOTEL 1000/10 SGB |  | No action |  | 10.0 | 0.4 | 1.0 | 10.5 | 1.1 | 0.11001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
109 | d9ca8f67a9e0461bba0911f7737ed542 | 1 MVA 10/0.4 kV DOTE 1000/10 SGB |  | No action |  | 10.0 | 0.4 | 1.0 | 10.5 | 1.7 | 0.17001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
110 | 65a987a23ba94b8fa88b9dc9f6ec64e7 | 1 MVA 10/0.4 kV 2.1 GEAFOL |  | No action |  | 10.0 | 0.4 | 1.0 | 7.5 | 2.1 | 0.21 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
111 | 4d06be7b9288423f97a9ac2838865abb | 1 MVA 10/0.4 kV 2 GEAFOL/FC |  | No action |  | 10.0 | 0.4 | 1.0 | 8.0 | 2.0 | 0.2 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
112 | 14518561d3894cb8b2c195e08821f739 | 1 MVA 10/0.4 kV 2 GEAFOL |  | No action |  | 10.0 | 0.4 | 1.0 | 7.9 | 2.0 | 0.2 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
113 | a32007efa4a143ac8e85e85dbcd03e19 | 1 MVA 10/0.4 kV 1.6 GEAFOL |  | No action |  | 10.0 | 0.4 | 1.0 | 9.2 | 1.6 | 0.16 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
114 | 45883389fc3548f9af6c60473e36ff0b | 1 MVA 10/0.4 kV 1.56 GEAFOL |  | No action |  | 10.0 | 0.4 | 1.0 | 8.2 | 1.56 | 0.156 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
115 | 7347e2aba99d4ac9a1c2c3a792454a18 | 0.8 MVA 10/0.4 kV Yyn6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.8 | 7.7 | 1.33 | 0.16626 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
116 | 465f4a458391498ebe35dfd48305e245 | 0.8 MVA 10/0.4 kV Yyn6 ASEA |  | No action |  | 10.0 | 0.4 | 0.8 | 7.7 | 1.7 | 0.21251 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
117 | 8dabeb0faeb64778925ca4cf1a9a44cf | 0.8 MVA 10/0.4 kV Yyn0 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.8 | 7.7 | 1.33 | 0.16626 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
118 | d064e1d2786f4c31b266aac8409c68cd | 0.8 MVA 10/0.4 kV Yyn0 ASEA |  | No action |  | 10.0 | 0.4 | 0.8 | 7.7 | 1.7 | 0.21251 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
119 | 9959ddeb7e1a4178997b22086fcb1051 | 0.8 MVA 10/0.4 kV Trafo Union wnr |  | No action |  | 10.0 | 0.4 | 0.8 | 7.0 | 1.35 | 0.16875 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
120 | 0a100556108f46219c8c0608fc7e4713 | 0.8 MVA 10/0.4 kV Trafo Union |  | No action |  | 10.0 | 0.4 | 0.8 | 6.9 | 1.7 | 0.2125 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
121 | 430183b084b342589b77d7e00cb26888 | 0.8 MVA 10/0.4 kV Dyn7 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.8 | 7.7 | 1.33 | 0.16626 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
122 | 21cc988dce4a4a5194ec3a16d933a6e0 | 0.8 MVA 10/0.4 kV Dyn7 ASEA |  | No action |  | 10.0 | 0.4 | 0.8 | 7.7 | 1.7 | 0.21251 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
123 | 9b4d84f66a57448285fe1a319b5efb4d | 0.8 MVA 10/0.4 kV Dyn5 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.8 | 7.7 | 1.33 | 0.16626 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
124 | ec557cc26c8c4db29aaf974f8fc7d84c | 0.8 MVA 10/0.4 kV Dyn5 ASEA |  | No action |  | 10.0 | 0.4 | 0.8 | 7.7 | 1.7 | 0.21251 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
125 | 2a9ee4db3e9c4bef87a3a6580457aa49 | 0.8 MVA 10/0.4 kV Dyn11 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.8 | 7.7 | 1.33 | 0.16626 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
126 | 6c42de8d000c4c4fa29a726b5db21e57 | 0.8 MVA 10/0.4 kV Dyn11 ASEA |  | No action |  | 10.0 | 0.4 | 0.8 | 7.7 | 1.7 | 0.21251 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
127 | 8ab903aad6754ca78844dc5753fb4652 | 0.8 MVA 10/0.4 kV Dyn1 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.8 | 7.7 | 1.33 | 0.16626 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
128 | c093bf7c4dd44f40853c88ed8e490ac5 | 0.8 MVA 10/0.4 kV Dyn1 ASEA |  | No action |  | 10.0 | 0.4 | 0.8 | 7.7 | 1.7 | 0.21251 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
129 | cbfef3a553914e8b8a95f0fe02f06a71 | 0.8 MVA 10/0.4 kV DTTHL SGB |  | No action |  | 10.0 | 0.4 | 0.8 | 7.0 | 1.3 | 0.16251 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
130 | 7f6b0588970547c69791db6ff2f7c6db | 0.8 MVA 10/0.4 kV DTTHIL SGB |  | No action |  | 10.0 | 0.4 | 0.8 | 5.0 | 1.45 | 0.18126 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
131 | 169bb9beac924e84b3a6b3dfd09be177 | 0.8 MVA 10/0.4 kV DTTH SGB |  | No action |  | 10.0 | 0.4 | 0.8 | 7.5 | 1.65 | 0.20626 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
132 | 8f19bd08307b40d6a9116642fda9cc8a | 0.8 MVA 10/0.4 kV DT 800/10 F SGB |  | No action |  | 10.0 | 0.4 | 0.8 | 7.8 | 1.7 | 0.21251 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
133 | a389094bf6d64355936144a87797a1c4 | 0.8 MVA 10/0.4 kV DOTEL 800/10 SGB |  | No action |  | 10.0 | 0.4 | 0.8 | 8.5 | 0.98 | 0.12251 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
134 | 05a244eab3fb46af869a8f2178eccf69 | 0.8 MVA 10/0.4 kV DOTE 800/10 SGB |  | No action |  | 10.0 | 0.4 | 0.8 | 8.5 | 1.5 | 0.18751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
135 | 2a64846b151a492eb1a8c2b5fc6ceca7 | 0.8 MVA 10/0.4 kV 1.8 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.8 | 6.6 | 1.8 | 0.225 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
136 | 5703856da239484ab8c32b25de8208a2 | 0.8 MVA 10/0.4 kV 1.7 GEAFOL/FC |  | No action |  | 10.0 | 0.4 | 0.8 | 6.8 | 1.7 | 0.2125 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
137 | 9a6852ae84ea4f3c9a9ec9ae5649adce | 0.8 MVA 10/0.4 kV 1.7 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.8 | 6.6 | 1.7 | 0.2125 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
138 | ac343f249a104111aebdd9892560f732 | 0.8 MVA 10/0.4 kV 1.4 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.8 | 7.7 | 1.4 | 0.175 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
139 | 725679580d0144c2bb65ab167ad3d4c6 | 0.8 MVA 10/0.4 kV 1.33 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.8 | 7.7 | 1.33 | 0.16625 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
140 | c805a6b292644066b9adb0cd97b1e481 | 0.63 MVA 10/0.4 kV Yyn6 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.6 | 1.1 | 0.174613 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
141 | 741e82312219480f88cc63369490bc96 | 0.63 MVA 10/0.4 kV Yyn6 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.6 | 1.4 | 0.222232 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
142 | dabec38e6f284f84bdc320a82abf544e | 0.63 MVA 10/0.4 kV Yyn6 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.4 | 1.15 | 0.18255 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
143 | afb856471a4744a2a383362b628cc509 | 0.63 MVA 10/0.4 kV Yyn6 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.4 | 1.5 | 0.238105 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
144 | 4932d53223204d9bb3c298dffa27d170 | 0.63 MVA 10/0.4 kV Yyn0 6wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.6 | 1.1 | 0.174613 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
145 | d54042f51af8403f9b2191f0e74f5708 | 0.63 MVA 10/0.4 kV Yyn0 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.6 | 1.4 | 0.222232 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
146 | 8c9752b2bd8743c79837ceb9dc785896 | 0.63 MVA 10/0.4 kV Yyn0 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.4 | 1.15 | 0.18255 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
147 | 670c80a9ee4646aaa547cf1124d4ba8d | 0.63 MVA 10/0.4 kV Yyn0 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.4 | 1.5 | 0.238105 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
148 | 527439d8ce5f4857afb0a7d1f557bdb6 | 0.63 MVA 10/0.4 kV Trafo Union wnr |  | No action |  | 10.0 | 0.4 | 0.63 | 6.8 | 1.18 | 0.1873016 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
149 | d1cdd3af5abe4733872385e832970367 | 0.63 MVA 10/0.4 kV Trafo Union |  | No action |  | 10.0 | 0.4 | 0.63 | 6.3 | 1.55 | 0.2460317 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
150 | 3cf205c01136484dbc307ab60491df98 | 0.63 MVA 10/0.4 kV Dyn7 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.6 | 1.1 | 0.174613 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
151 | 2139c0f418454b4dac52c22071bf86b1 | 0.63 MVA 10/0.4 kV Dyn7 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.6 | 1.4 | 0.222232 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
152 | 41a2798c6edf41fbafe3bdb410829602 | 0.63 MVA 10/0.4 kV Dyn7 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.4 | 1.15 | 0.18255 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
153 | 1028e953eaf14ff2964d3bd712916edf | 0.63 MVA 10/0.4 kV Dyn7 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.4 | 1.5 | 0.238105 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
154 | 1a2165f4e5f14c8faf3785d269e3c3c6 | 0.63 MVA 10/0.4 kV Dyn5 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.6 | 1.1 | 0.174613 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
155 | 9a16a051234640cc9be34b14f32e9775 | 0.63 MVA 10/0.4 kV Dyn5 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.6 | 1.4 | 0.222232 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
156 | b00a93fe898e4339b1d869165a865617 | 0.63 MVA 10/0.4 kV Dyn5 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.4 | 1.15 | 0.18255 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
157 | 768a25e93d1843079147dcc1d8b1c9bc | 0.63 MVA 10/0.4 kV Dyn5 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.4 | 1.5 | 0.238105 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
158 | 4cbc4642d9ce405d919049adb7fcfc6c | 0.63 MVA 10/0.4 kV Dyn11 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.6 | 1.1 | 0.174613 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
159 | 694017997f26497ab09ea4029c82ebbd | 0.63 MVA 10/0.4 kV Dyn11 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.6 | 1.4 | 0.222232 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
160 | 1d5fe1faf5b44e48984dfd57d7be4d23 | 0.63 MVA 10/0.4 kV Dyn11 4wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.4 | 1.15 | 0.18255 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
161 | 47e9749292ba4213b2c4bbc27b95513f | 0.63 MVA 10/0.4 kV Dyn11 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.4 | 1.5 | 0.238105 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
162 | ed6407ed7c084c059136d0801c9d8c84 | 0.63 MVA 10/0.4 kV Dyn1 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.6 | 1.1 | 0.174613 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
163 | 2ba463f23ff54c8d8b67e848c15fc0b9 | 0.63 MVA 10/0.4 kV Dyn1 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.6 | 1.4 | 0.222232 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
164 | 44de78cc5e7e444fa8d9cb630b61f913 | 0.63 MVA 10/0.4 kV Dyn1 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.4 | 1.15 | 0.18255 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
165 | d339e4e8bc774e28b0669da27a51648b | 0.63 MVA 10/0.4 kV Dyn1 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.63 | 6.4 | 1.5 | 0.238105 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
166 | 85c92ad1672946c1ac735284bd4315e4 | 0.63 MVA 10/0.4 kV DTTHYL SGB |  | No action |  | 10.0 | 0.4 | 0.63 | 6.0 | 0.95 | 0.150804 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
167 | 3e07aa11f87445acb4dc30ce059c6f31 | 0.63 MVA 10/0.4 kV DTTHL SGB |  | No action |  | 10.0 | 0.4 | 0.63 | 6.4 | 1.12 | 0.177788 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
168 | e8a5c5f562734466a5a8c97f0677751d | 0.63 MVA 10/0.4 kV DTTH SGB |  | No action |  | 10.0 | 0.4 | 0.63 | 6.4 | 1.4 | 0.222232 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
169 | 27555deec1b645b38ab3f2e52f0c1857 | 0.63 MVA 10/0.4 kV DTKa SGB |  | No action |  | 10.0 | 0.4 | 0.63 | 6.5 | 1.65 | 0.261915 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
170 | 93ace2d83f184778866963c6d27518c5 | 0.63 MVA 10/0.4 kV DT 630/10 F SGB |  | No action |  | 10.0 | 0.4 | 0.63 | 6.5 | 1.45 | 0.230169 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
171 | 361f518b1cba43cba86c3591c59d23c0 | 0.63 MVA 10/0.4 kV DT 630 SGB |  | No action |  | 10.0 | 0.4 | 0.63 | 6.6 | 1.6 | 0.253978 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
172 | 2183d92387574e3da13f09894031bd25 | 0.63 MVA 10/0.4 kV DOTNL 630/10 SGB |  | No action |  | 10.0 | 0.4 | 0.63 | 8.4 | 0.88 | 0.139693 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
173 | bc89955bcac7475994782b773339ee2a | 0.63 MVA 10/0.4 kV DOTN 630/10 SGB |  | No action |  | 10.0 | 0.4 | 0.63 | 8.4 | 1.15 | 0.18255 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
174 | c6aadee050ae43098dbe1b905b0c980c | 0.63 MVA 10/0.4 kV DOTEL 630/10 SGB |  | No action |  | 10.0 | 0.4 | 0.63 | 6.5 | 0.85 | 0.134931 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
175 | e3a271cbafb14eaf85060c599ecca12a | 0.63 MVA 10/0.4 kV DOTE 630/10 SGB |  | No action |  | 10.0 | 0.4 | 0.63 | 6.5 | 1.3 | 0.206359 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
176 | 0e6a5a38ae26421d84b97e9dd97140bb | 0.63 MVA 10/0.4 kV 1.5 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.63 | 5.8 | 1.5 | 0.2380952 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
177 | d2608d22cff74e87b6cf63b9613ae8dd | 0.63 MVA 10/0.4 kV 1.4 GEAFOL/FC |  | No action |  | 10.0 | 0.4 | 0.63 | 6.1 | 1.4 | 0.2222222 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
178 | 43c43334b0c14d2db7a76245e85aac43 | 0.63 MVA 10/0.4 kV 1.4 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.63 | 5.6 | 1.4 | 0.2222222 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
179 | b151191153a34373b0b5183953507db6 | 0.63 MVA 10/0.4 kV 1.17 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.63 | 6.4 | 1.17 | 0.1857143 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
180 | 0eb0206126be41658668c8f8e1207c9b | 0.63 MVA 10/0.4 kV 1.09 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.63 | 6.4 | 1.09 | 0.1730159 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
181 | 032facd0b2a94934b0ae0cbd744d6e0d | 0.5 MVA 10/0.4 kV Yyn6 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.7 | 0.94 | 0.18801 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
182 | 06c50b20fc6a43b8b2b01a0d64e1ff9f | 0.5 MVA 10/0.4 kV Yyn6 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.7 | 1.2 | 0.24001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
183 | eeaab11492c84479b4a057099c491a5a | 0.5 MVA 10/0.4 kV Yyn6 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.5 | 1.0 | 0.20001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
184 | 9c8afce66c104ac097d7a536388cbb68 | 0.5 MVA 10/0.4 kV Yyn6 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.5 | 1.3 | 0.26001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
185 | 53b40004b15946098df80b9ddb0ed6f7 | 0.5 MVA 10/0.4 kV Yyn0 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.7 | 0.94 | 0.18801 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
186 | 5e3e0d792993455fb57f23e16a60debc | 0.5 MVA 10/0.4 kV Yyn0 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.7 | 1.2 | 0.24001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
187 | 2fdff9e1f5cf497d88802a2ec8bf6996 | 0.5 MVA 10/0.4 kV Yyn0 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.5 | 1.0 | 0.20001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
188 | f3769de0aac047bfa7588f4dbfffbb0a | 0.5 MVA 10/0.4 kV Yyn0 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.5 | 1.3 | 0.26001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
189 | 5edf7debf2104c0cb451b8190807e054 | 0.5 MVA 10/0.4 kV Trafo Union wnr |  | No action |  | 10.0 | 0.4 | 0.5 | 5.5 | 1.07 | 0.214 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
190 | d0e31273104e4568b7a0a07e91121593 | 0.5 MVA 10/0.4 kV Trafo Union |  | No action |  | 10.0 | 0.4 | 0.5 | 5.2 | 1.38 | 0.276 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
191 | cf19d3034ac64bcaaf1bcb5452a9abe8 | 0.5 MVA 10/0.4 kV Dyn7 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.7 | 0.94 | 0.18801 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
192 | dfbf91001d214f23ac39fe3e7776c86b | 0.5 MVA 10/0.4 kV Dyn7 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.7 | 1.2 | 0.24001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
193 | d1305d3cdd82432fae93e824f29d712f | 0.5 MVA 10/0.4 kV Dyn7 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.5 | 1.0 | 0.20001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
194 | a7754d67e08c440f89d88fdeb9edda63 | 0.5 MVA 10/0.4 kV Dyn7 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.5 | 1.3 | 0.26001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
195 | 666d130f3fba4e25a58b9261182fca50 | 0.5 MVA 10/0.4 kV Dyn5 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.7 | 0.94 | 0.18801 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
196 | 37e58669df274767b16515945e48dd9b | 0.5 MVA 10/0.4 kV Dyn5 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.7 | 1.2 | 0.24001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
197 | 810e969c8bff492abd0be59d5b21e2c1 | 0.5 MVA 10/0.4 kV Dyn5 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.5 | 1.0 | 0.20001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
198 | eb5b63221e2b4e8cac794f0260be923c | 0.5 MVA 10/0.4 kV Dyn5 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.5 | 1.3 | 0.26001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
199 | e9146f8c4078437e8b9d6b07e0d4bcb8 | 0.5 MVA 10/0.4 kV Dyn11 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.7 | 0.94 | 0.18801 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
200 | b8695a5decc54b5a953098c106ff3be8 | 0.5 MVA 10/0.4 kV Dyn11 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.7 | 1.2 | 0.24001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
201 | b3eb1580f1e641b4906546f9c4076c61 | 0.5 MVA 10/0.4 kV Dyn11 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.5 | 1.0 | 0.20001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
202 | 23f46d4384bb49bcb181237a83744807 | 0.5 MVA 10/0.4 kV Dyn11 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.5 | 1.3 | 0.26001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
203 | 1089deddda1e4bad8db055d8cd27c3a6 | 0.5 MVA 10/0.4 kV Dyn1 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.7 | 0.94 | 0.18801 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
204 | 137da244087c4954a9e2199841986041 | 0.5 MVA 10/0.4 kV Dyn1 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.7 | 1.2 | 0.24001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
205 | 857947e8073b44d493d7033fdf5e5450 | 0.5 MVA 10/0.4 kV Dyn1 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.5 | 1.0 | 0.20001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
206 | d99f530caa0f4d0da61647239eda3cd1 | 0.5 MVA 10/0.4 kV Dyn1 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.5 | 5.5 | 1.3 | 0.26001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
207 | 35e74a0ae85d41c59b274529b91c4e34 | 0.5 MVA 10/0.4 kV DTTHYL SGB |  | No action |  | 10.0 | 0.4 | 0.5 | 5.3 | 0.82 | 0.16401 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
208 | 3706e962593743e1beb42dd4d2fd2ca3 | 0.5 MVA 10/0.4 kV DTTHL SGB |  | No action |  | 10.0 | 0.4 | 0.5 | 5.1 | 0.95 | 0.19001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
209 | 177cd09831da49bfae09611759b3bac2 | 0.5 MVA 10/0.4 kV DTTH SGB |  | No action |  | 10.0 | 0.4 | 0.5 | 5.1 | 1.2 | 0.24001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
210 | 6a7d7919cbd5448b98d0cdd5f68511c6 | 0.5 MVA 10/0.4 kV DT 500/10 F SGB |  | No action |  | 10.0 | 0.4 | 0.5 | 5.5 | 1.3 | 0.26001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
211 | 0e6eaf5ea7274330a17673918545c26a | 0.5 MVA 10/0.4 kV DT 500 SGB |  | No action |  | 10.0 | 0.4 | 0.5 | 5.4 | 1.4 | 0.28001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
212 | afe8a8ef7ea34c2c8a13faffddc79142 | 0.5 MVA 10/0.4 kV DOTNL 500/10 SGB |  | No action |  | 10.0 | 0.4 | 0.5 | 7.15 | 0.75 | 0.15001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
213 | fe332dba35034d3aad4b2de4727b6db3 | 0.5 MVA 10/0.4 kV DOTN 500/10 SGB |  | No action |  | 10.0 | 0.4 | 0.5 | 7.15 | 0.98 | 0.19601 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
214 | 99f3199ce46447f791fec945fe80271e | 0.5 MVA 10/0.4 kV DOTEL 500/10 SGB |  | No action |  | 10.0 | 0.4 | 0.5 | 5.5 | 0.72 | 0.14401 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
215 | 0fd9445ebc33450a89a40f1f80b01e30 | 0.5 MVA 10/0.4 kV DOTE 500/10 SGB |  | No action |  | 10.0 | 0.4 | 0.5 | 5.5 | 1.1 | 0.22001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
216 | 5e99234cb3f448ba845aa49dfde5322c | 0.5 MVA 10/0.4 kV 1.3 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.5 | 4.2 | 1.3 | 0.26 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
217 | 5896179d10464769a007be9ac47fa7c6 | 0.5 MVA 10/0.4 kV 1.2 GEAFOL/FC |  | No action |  | 10.0 | 0.4 | 0.5 | 5.2 | 1.2 | 0.24 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
218 | 5201a38ce08f44749ab1887610f4c2ad | 0.5 MVA 10/0.4 kV 1.2 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.5 | 5.0 | 1.2 | 0.24 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
219 | 517d0f1162584646b80882863af94054 | 0.5 MVA 10/0.4 kV 1.01 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.5 | 4.8 | 1.01 | 0.202 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
220 | d287f893362f442da6db5d5a044438ba | 0.5 MVA 10/0.4 kV 0.94 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.5 | 4.7 | 0.94 | 0.188 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
221 | 25134bd1b48040d49f472a10a73beec6 | 0.4 MVA 10/0.4 kV Yyn6 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 5.0 | 0.78 | 0.19501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
222 | 70049ad1bbc04e589303fe81199b3bb8 | 0.4 MVA 10/0.4 kV Yyn6 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 5.0 | 1.0 | 0.25001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
223 | f3236075ae5e4f4bb940ae942c312a98 | 0.4 MVA 10/0.4 kV Yyn6 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 4.3 | 0.88 | 0.22001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
224 | 6dc343a78c444599ba42410b5b1ee523 | 0.4 MVA 10/0.4 kV Yyn6 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 4.3 | 1.15 | 0.28751 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
225 | 61cb5ef6e204484db597657aa5ca1df9 | 0.4 MVA 10/0.4 kV Yyn0 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 5.0 | 0.78 | 0.19501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
226 | 1e10315e88c548a8b4fe8dd2244720aa | 0.4 MVA 10/0.4 kV Yyn0 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 5.0 | 1.0 | 0.25001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
227 | 5bf4403d30884cb3a2d7157f7efecd3f | 0.4 MVA 10/0.4 kV Yyn0 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 4.3 | 0.88 | 0.22001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
228 | 17f934171a334cdb9e2c40cf7c9b6148 | 0.4 MVA 10/0.4 kV Yyn0 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 4.3 | 1.15 | 0.28751 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
229 | 27867d29307c4254b5afe80836d2074c | 0.4 MVA 10/0.4 kV Trafo Union wnr |  | No action |  | 10.0 | 0.4 | 0.4 | 5.3 | 0.95 | 0.2375 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
230 | 6086a6432fa345848dc72ccaa6808b48 | 0.4 MVA 10/0.4 kV Trafo Union |  | No action |  | 10.0 | 0.4 | 0.4 | 5.0 | 1.22 | 0.305 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
231 | 5fb7d224d28f400f86216e8ab344465a | 0.4 MVA 10/0.4 kV Dyn7 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 5.0 | 0.78 | 0.19501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
232 | 3a3eecb61bc24145a0123ddc03567664 | 0.4 MVA 10/0.4 kV Dyn7 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 5.0 | 1.0 | 0.25001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
233 | 0d75c58572bd4d8281ba64798567022e | 0.4 MVA 10/0.4 kV Dyn7 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 4.3 | 0.88 | 0.22001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
234 | 278a6b2adfda4834b225f0bd67fca47b | 0.4 MVA 10/0.4 kV Dyn7 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 4.3 | 1.15 | 0.28751 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
235 | 61575c9f3d604644b38b0ba4087b80d3 | 0.4 MVA 10/0.4 kV Dyn5 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 5.0 | 0.78 | 0.19501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
236 | 3c5f294c83674d90ad3ffe3ac479a2be | 0.4 MVA 10/0.4 kV Dyn5 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 5.0 | 1.0 | 0.25001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
237 | 0896f0c0b5704dd4a40e64a5b7f32b37 | 0.4 MVA 10/0.4 kV Dyn5 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 4.3 | 0.88 | 0.22001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
238 | a237344975d14cd1856e53a00a18ee02 | 0.4 MVA 10/0.4 kV Dyn5 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 4.3 | 1.15 | 0.28751 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
239 | 12b11ee4de384c6daca7394ee4b81c04 | 0.4 MVA 10/0.4 kV Dyn11 6wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 5.0 | 0.78 | 0.19501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
240 | 234f918f235e42b2866dbdd7cd286d23 | 0.4 MVA 10/0.4 kV Dyn11 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 5.0 | 1.0 | 0.25001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
241 | 2e34e7f2dc7c497a82b417ea3828f1c4 | 0.4 MVA 10/0.4 kV Dyn11 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 4.3 | 0.88 | 0.22001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
242 | a26a8f7b8f9b4ea6b41a86fe22af4cd6 | 0.4 MVA 10/0.4 kV Dyn11 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 4.3 | 1.15 | 0.28751 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
243 | e47d0eeba95541ccb166544e5f983b01 | 0.4 MVA 10/0.4 kV Dyn1 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 5.0 | 0.78 | 0.19501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
244 | 43dd50e2d17d41e59946c8227208aef1 | 0.4 MVA 10/0.4 kV Dyn1 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 5.0 | 1.0 | 0.25001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
245 | 4e75a535df424abe9de2e0ee144c5b0b | 0.4 MVA 10/0.4 kV Dyn1 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 4.3 | 0.88 | 0.22001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
246 | a90e5087eecc455c81ea5ea10d69f750 | 0.4 MVA 10/0.4 kV Dyn1 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.4 | 4.3 | 1.15 | 0.28751 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
247 | 0d196039bc204c7ebf660e6da706575c | 0.4 MVA 10/0.4 kV DTTHYL SGB |  | No action |  | 10.0 | 0.4 | 0.4 | 4.3 | 0.67 | 0.16751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
248 | 10060c01aada44adae207a8b3503f180 | 0.4 MVA 10/0.4 kV DTTHL SGB |  | No action |  | 10.0 | 0.4 | 0.4 | 4.3 | 0.83 | 0.20751 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
249 | 12bbfc565f7b4d268702d52d237214cb | 0.4 MVA 10/0.4 kV DTTH SGB |  | No action |  | 10.0 | 0.4 | 0.4 | 4.3 | 1.05 | 0.26251 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
250 | dfa0835c790c428f8bbcb63a100092aa | 0.4 MVA 10/0.4 kV DTKa SGB |  | No action |  | 10.0 | 0.4 | 0.4 | 4.5 | 1.2 | 0.30001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
251 | 4b405ba030474a55a83e1e0ed2d12ad1 | 0.4 MVA 10/0.4 kV DT 400/10 F SGB |  | No action |  | 10.0 | 0.4 | 0.4 | 4.6 | 1.15 | 0.28751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
252 | 9b82e997a98140a4bfc8c0aa5703d1c8 | 0.4 MVA 10/0.4 kV DT 400 SGB |  | No action |  | 10.0 | 0.4 | 0.4 | 4.6 | 1.25 | 0.31251 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
253 | 10f8193a42aa4c2b976c9a8b2d2eda95 | 0.4 MVA 10/0.4 kV DOTNL 400/10 SGB |  | No action |  | 10.0 | 0.4 | 0.4 | 6.0 | 0.625 | 0.15626 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
254 | dab01446887f45d4af2f19e17792f27d | 0.4 MVA 10/0.4 kV DOTN 400/10 SGB |  | No action |  | 10.0 | 0.4 | 0.4 | 6.0 | 0.815 | 0.20376 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
255 | 9e7e4ecb2b094334a66c865afb13aa6d | 0.4 MVA 10/0.4 kV DOTEL 400/10 SGB |  | No action |  | 10.0 | 0.4 | 0.4 | 4.6 | 0.6 | 0.15001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
256 | 5a499bdb7b4841c4880d7b751504a5d7 | 0.4 MVA 10/0.4 kV DOTE 400/10 SGB |  | No action |  | 10.0 | 0.4 | 0.4 | 4.6 | 0.93 | 0.23251 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
257 | df9e0497f3d34a9495046f5027fddcc2 | 0.4 MVA 10/0.4 kV 1.15 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.4 | 3.7 | 1.15 | 0.2875 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
258 | fe5b73a2b6c94b1382d282be3b5d73be | 0.4 MVA 10/0.4 kV 1 GEAFOL/FC |  | No action |  | 10.0 | 0.4 | 0.4 | 4.4 | 1.0 | 0.25 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
259 | ff09cf17eed149c7852e0cc5fa48cb64 | 0.4 MVA 10/0.4 kV 1 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.4 | 3.9 | 1.0 | 0.25 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
260 | 0876d504a09f478bbac2116eb791a24c | 0.4 MVA 10/0.4 kV 0.9 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.4 | 4.3 | 0.9 | 0.225 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
261 | 2a20723574454205b88ae0a0167ca429 | 0.4 MVA 10/0.4 kV 0.78 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.4 | 4.1 | 0.78 | 0.195 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
262 | 88dfab8c231b4d19b74c09b7883bfba6 | 0.315 MVA 10/0.4 kV Yyn6 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 4.1 | 0.64 | 0.203185 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
263 | 26c97fc738384fb0bc3be7e42490f3ec | 0.315 MVA 10/0.4 kV Yyn6 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 4.1 | 0.82 | 0.260327 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
264 | c3cd209d5ce243bd95eac983eac4e417 | 0.315 MVA 10/0.4 kV Yyn6 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 3.65 | 0.73 | 0.231756 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
265 | e156e47c32c24fc0a5c8907a5f657d62 | 0.315 MVA 10/0.4 kV Yyn6 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 3.65 | 0.95 | 0.301597 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
266 | 5a5fa4a845d0456db34f64a353ea0275 | 0.315 MVA 10/0.4 kV Yyn0 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 4.1 | 0.64 | 0.203185 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
267 | 2f68939ee1764dd28c2571fe8b02b004 | 0.315 MVA 10/0.4 kV Yyn0 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 4.1 | 0.82 | 0.260327 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
268 | 5c19a32382304b999b514e56852344e5 | 0.315 MVA 10/0.4 kV Yyn0 4wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 3.65 | 0.73 | 0.231756 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
269 | 41ec60f514954001bc798da081fde038 | 0.315 MVA 10/0.4 kV Yyn0 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 3.65 | 0.95 | 0.301597 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
270 | 05092606977e48d5b7d7e9cc6dd99c67 | 0.315 MVA 10/0.4 kV Trafo Union wnr |  | No action |  | 10.0 | 0.4 | 0.315 | 4.2 | 0.87 | 0.2761905 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
271 | d4885939e76f43039eda21c5649bf40b | 0.315 MVA 10/0.4 kV Trafo Union |  | No action |  | 10.0 | 0.4 | 0.315 | 4.0 | 1.12 | 0.3555556 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
272 | 64b5c5c19f4a4d12a79f2bd20eb9a8c1 | 0.315 MVA 10/0.4 kV Dyn7 6wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 4.1 | 0.64 | 0.203185 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
273 | 7a58d3a62d974f0ebdcb8e1eff68f2cd | 0.315 MVA 10/0.4 kV Dyn7 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 4.1 | 0.82 | 0.260327 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
274 | 1eea7a88cad94ad1995a18ca3d932844 | 0.315 MVA 10/0.4 kV Dyn7 4wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 3.65 | 0.73 | 0.231756 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
275 | 235aa36b78544f44ac164c2bb666f912 | 0.315 MVA 10/0.4 kV Dyn7 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 3.65 | 0.95 | 0.301597 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
276 | 333fcc1dd4dc43c697f826af2553f58a | 0.315 MVA 10/0.4 kV Dyn5 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 4.1 | 0.64 | 0.203185 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
277 | 64392a6ad5db4d169d41eb1c60eae96f | 0.315 MVA 10/0.4 kV Dyn5 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 4.1 | 0.82 | 0.260327 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
278 | ea61474feea3401ca41d168752a12717 | 0.315 MVA 10/0.4 kV Dyn5 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 3.65 | 0.73 | 0.231756 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
279 | 76580d9ed9fd43ba8b77fdf15f51978a | 0.315 MVA 10/0.4 kV Dyn5 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 3.65 | 0.95 | 0.301597 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
280 | fd051ac3bfad49e89de473c8739fecf3 | 0.315 MVA 10/0.4 kV Dyn11 6wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 4.1 | 0.64 | 0.203185 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
281 | 2a241c7fc7dc4bd9b061b53583d32b81 | 0.315 MVA 10/0.4 kV Dyn11 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 4.1 | 0.82 | 0.260327 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
282 | a6584151237040bd94a939d3cdba7fca | 0.315 MVA 10/0.4 kV Dyn11 4wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 3.65 | 0.73 | 0.231756 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
283 | dbd52a7df1714e7bb1ce6cf05d1ab916 | 0.315 MVA 10/0.4 kV Dyn11 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 3.65 | 0.95 | 0.301597 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
284 | 1191b4c7dd24424799e0710cca4059cc | 0.315 MVA 10/0.4 kV Dyn1 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 4.1 | 0.64 | 0.203185 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
285 | ee79e831690f439c975eacab161c7fa3 | 0.315 MVA 10/0.4 kV Dyn1 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 4.1 | 0.82 | 0.260327 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
286 | 64ed73073a074b1882b075aae70295fa | 0.315 MVA 10/0.4 kV Dyn1 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 3.65 | 0.73 | 0.231756 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
287 | 7e25989a618947a686df01e5cbcd4a23 | 0.315 MVA 10/0.4 kV Dyn1 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.315 | 3.65 | 0.95 | 0.301597 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
288 | e704b09d4f854c068839cdcafa361638 | 0.315 MVA 10/0.4 kV DT 315/10 F SGB |  | No action |  | 10.0 | 0.4 | 0.315 | 4.0 | 0.95 | 0.301597 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
289 | 56ea366b10f74bc39caf176bac34a392 | 0.315 MVA 10/0.4 kV DT 315 SGB |  | No action |  | 10.0 | 0.4 | 0.315 | 4.0 | 1.0 | 0.31747 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
290 | 8d3f793211e14d3088d3960da115822a | 0.315 MVA 10/0.4 kV DOTNL 315/10 SGB |  | No action |  | 10.0 | 0.4 | 0.315 | 4.9 | 0.52 | 0.165089 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
291 | 79e63534df01456c84214b95e9d6dccd | 0.315 MVA 10/0.4 kV DOTN 315/10 SGB |  | No action |  | 10.0 | 0.4 | 0.315 | 4.9 | 0.68 | 0.215883 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
292 | 6f76f75fd6e247cf90e6710d9fabf035 | 0.315 MVA 10/0.4 kV DOTE 315/10 SGB |  | No action |  | 10.0 | 0.4 | 0.315 | 3.9 | 0.77 | 0.244454 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
293 | e9b46b33bca74de3ba326f973c29e322 | 0.315 MVA 10/0.4 kV 0.95 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.315 | 3.5 | 0.95 | 0.3015873 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
294 | d16b0e7209814c10b918ad812a124875 | 0.315 MVA 10/0.4 kV 0.82 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.315 | 3.4 | 0.82 | 0.2603175 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
295 | 1408fb9461354716b53afae3a68fd37a | 0.315 MVA 10/0.4 kV 0.74 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.315 | 3.6 | 0.74 | 0.2349206 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
296 | 76ead7b96f134c1f81375a0b951be003 | 0.315 MVA 10/0.4 kV 0.64 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.315 | 3.8 | 0.64 | 0.2031746 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
297 | cf5a108eef5f44978a40ca3fabdf6630 | 0.315 MVA 0.4/10kV DOTEL 315/10 SGB |  | No action |  | 10.0 | 0.4 | 0.315 | 3.9 | 0.5 | 0.15874 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
298 | 46431b0975734c10b1a15570ffa0ed5a | 0.25 MVA 10/0.4 kV Yyn6 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.4 | 0.54 | 0.21601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
299 | 2d6d8b832a2d4f70b0eca04d1bdba1d7 | 0.25 MVA 10/0.4 kV Yyn6 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.4 | 0.69 | 0.27601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
300 | 7d693e5786b749d4b7e3bf0123d8ef25 | 0.25 MVA 10/0.4 kV Yyn6 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.0 | 0.62 | 0.24801 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
301 | 2fae346203cb4d5d88208046f60e3c08 | 0.25 MVA 10/0.4 kV Yyn6 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.0 | 0.82 | 0.32801 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
302 | d897de632447460b87c5457b5499bdf5 | 0.25 MVA 10/0.4 kV Yyn0 6wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.4 | 0.54 | 0.21601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
303 | f1b2affe03a34f10bb18545c4dbc2c9b | 0.25 MVA 10/0.4 kV Yyn0 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.4 | 0.69 | 0.27601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
304 | bd1bc822a30c4372a39cccddd68701d1 | 0.25 MVA 10/0.4 kV Yyn0 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.0 | 0.62 | 0.24801 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
305 | 1a8e7b25f6c94b979b34e4c7d0a55ff9 | 0.25 MVA 10/0.4 kV Yyn0 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.0 | 0.82 | 0.32801 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
306 | 45e4faa184804a7dad80118846b152d6 | 0.25 MVA 10/0.4 kV ET 250/23 SGB |  | No action |  | 10.0 | 0.4 | 0.25 | 3.0 | 0.82 | 0.32801 | 3.75 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
307 | c03620f5ad3246b0867e867e4983ef13 | 0.25 MVA 10/0.4 kV ET 250 SGB |  | No action |  | 10.0 | 0.4 | 0.25 | 3.0 | 0.82 | 0.32801 | 3.75 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
308 | 27d0e5e1b8f54a139d45c71adb14315a | 0.25 MVA 10/0.4 kV Dyn7 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.4 | 0.54 | 0.21601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
309 | b8ffd948028d42e383f5fe44a7f4314c | 0.25 MVA 10/0.4 kV Dyn7 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.4 | 0.69 | 0.27601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
310 | 3ebcaab53bee4724b9275aefe0356d35 | 0.25 MVA 10/0.4 kV Dyn7 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.0 | 0.62 | 0.24801 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
311 | 469f73b7df6f47088bff38259bf6d88c | 0.25 MVA 10/0.4 kV Dyn7 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.0 | 0.82 | 0.32801 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
312 | 7a83d1fe5e7a4db3bc105f83591a1217 | 0.25 MVA 10/0.4 kV Dyn5 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.4 | 0.54 | 0.21601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
313 | 9cfe4f11ebf14324bdbede1d4f68828e | 0.25 MVA 10/0.4 kV Dyn5 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.4 | 0.69 | 0.27601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
314 | f876ea308ecf4211b440d64580b84b99 | 0.25 MVA 10/0.4 kV Dyn5 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.0 | 0.62 | 0.24801 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
315 | 02d51de667284a24b4987239e09bd55d | 0.25 MVA 10/0.4 kV Dyn5 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.0 | 0.82 | 0.32801 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
316 | d38fa6e1ba0646e0b073830c657293c1 | 0.25 MVA 10/0.4 kV Dyn11 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.4 | 0.54 | 0.21601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
317 | 2ff5984f4f374f52b607dc102b1befa6 | 0.25 MVA 10/0.4 kV Dyn11 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.4 | 0.69 | 0.27601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
318 | 29e5980383cd4144bcd92acb9b5d4266 | 0.25 MVA 10/0.4 kV Dyn11 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.0 | 0.62 | 0.24801 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
319 | fb4c1658e5be4deabbf039270dcef2c2 | 0.25 MVA 10/0.4 kV Dyn11 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.0 | 0.82 | 0.32801 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
320 | 2df879d059134b60b834db4b211cc9d5 | 0.25 MVA 10/0.4 kV Dyn1 6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.4 | 0.54 | 0.21601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
321 | 1233b5d8c951416d8bc597390f40157d | 0.25 MVA 10/0.4 kV Dyn1 6 ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.4 | 0.69 | 0.27601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
322 | 4bd68bd0b2174e3795813e984181af02 | 0.25 MVA 10/0.4 kV Dyn1 4 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.0 | 0.62 | 0.24801 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
323 | ddf82aca270144f2a486548fdf898820 | 0.25 MVA 10/0.4 kV Dyn1 4 ASEA |  | No action |  | 10.0 | 0.4 | 0.25 | 3.0 | 0.82 | 0.32801 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
324 | 7084366027614722b67510ee7fce63c3 | 0.25 MVA 10/0.4 kV DTTHL SGB |  | No action |  | 10.0 | 0.4 | 0.25 | 3.0 | 0.5 | 0.20001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
325 | 2400a02b5fed436fae10af30076aa770 | 0.25 MVA 10/0.4 kV DTKa SGB |  | No action |  | 10.0 | 0.4 | 0.25 | 3.2 | 0.8 | 0.32001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
326 | efbeda0bfdd1401383ed83dc329e7ac2 | 0.25 MVA 10/0.4 kV DT 250/10 F SGB |  | No action |  | 10.0 | 0.4 | 0.25 | 3.4 | 0.8 | 0.32001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
327 | e68357331c824a30afb0f9114e579e78 | 0.25 MVA 10/0.4 kV DT 250 SGB |  | No action |  | 10.0 | 0.4 | 0.25 | 3.2 | 0.9 | 0.36001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
328 | 3b3c17354ae3433ebb024fa62d06c778 | 0.25 MVA 10/0.4 kV DOTNL 250/10 SGB |  | No action |  | 10.0 | 0.4 | 0.25 | 4.1 | 0.435 | 0.17401 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
329 | 3e97931296134bd69047b2c2b851076a | 0.25 MVA 10/0.4 kV DOTN 250/10 SGB |  | No action |  | 10.0 | 0.4 | 0.25 | 4.1 | 0.57 | 0.22801 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
330 | 578f19ac35e0418f95a1bf025c86b755 | 0.25 MVA 10/0.4 kV DOTEL 250/10 SGB |  | No action |  | 10.0 | 0.4 | 0.25 | 3.25 | 0.42 | 0.16801 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
331 | 51e3d3d016e741a8bd912d7119ff64e1 | 0.25 MVA 10/0.4 kV DOTE 250/10 SGB |  | No action |  | 10.0 | 0.4 | 0.25 | 3.25 | 0.65 | 0.26001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
332 | c07b559381c84dfa9dd75d2942cd85cf | 0.25 MVA 10/0.4 kV 0.82 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.25 | 3.0 | 0.82 | 0.328 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
333 | 985f5cd0c4fa42ffaa75335d29355133 | 0.25 MVA 10/0.4 kV 0.77 Trafo Union |  | No action |  | 10.0 | 0.4 | 0.25 | 2.9 | 0.77 | 0.308 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
334 | aa450a2466b54c0081beab3c00b7ac0b | 0.25 MVA 10/0.4 kV 0.69 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.25 | 3.0 | 0.69 | 0.276 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
335 | 21fbaed821aa440b9c4926e7eda41b0f | 0.25 MVA 10/0.4 kV 0.64 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.25 | 3.0 | 0.64 | 0.256 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
336 | f59dfc85fccc4a58bf44e965bca76ad5 | 0.25 MVA 10/0.4 kV 0.6 Trafo Union wnr |  | No action |  | 10.0 | 0.4 | 0.25 | 3.0 | 0.6 | 0.24 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
337 | 9fd934fadc2c4459a839effc24708e43 | 0.25 MVA 10/0.4 kV 0.54 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.25 | 3.4 | 0.54 | 0.216 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
338 | 9ab5253518f4499d81166c1261429242 | 0.25 MVA 10/0.4 kV 0.5 Trafo Union |  | No action |  | 10.0 | 0.4 | 0.25 | 2.9 | 0.77 | 0.308 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
339 | 0da992fd7eca42c195de0d6b278ce69e | 0.25 MVA 10/0.4 kV 0.4 Trafo Union wnr |  | No action |  | 10.0 | 0.4 | 0.25 | 3.0 | 0.6 | 0.24 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
340 | c5de18024aa54fc2a5c029a4e6f021ea | 0.2 MVA 10/0.4 kV Yyn6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.2 | 2.75 | 0.52 | 0.26001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
341 | 561d8e17a53b49b181f43c617cbcaf44 | 0.2 MVA 10/0.4 kV Yyn6 ASEA |  | No action |  | 10.0 | 0.4 | 0.2 | 2.75 | 0.69 | 0.34501 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
342 | 3ce6369d0e3a4169a2b9d2d51d9d3cb5 | 0.2 MVA 10/0.4 kV Yyn0 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.2 | 2.75 | 0.52 | 0.26001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
343 | c208eb4824314eba9ddc35d6aef7d1de | 0.2 MVA 10/0.4 kV Yyn0 ASEA |  | No action |  | 10.0 | 0.4 | 0.2 | 2.75 | 0.69 | 0.34501 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
344 | 437c79e6a2f1414c956eca252fc8e9a2 | 0.2 MVA 10/0.4 kV Trafo Union wnr |  | No action |  | 10.0 | 0.4 | 0.2 | 2.5 | 0.55 | 0.275 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
345 | 4a682728f2f5459a9b156ceff0ff8002 | 0.2 MVA 10/0.4 kV Trafo Union |  | No action |  | 10.0 | 0.4 | 0.2 | 2.5 | 0.7 | 0.35 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
346 | c004e479ea574e0fbc72a27df812d70e | 0.2 MVA 10/0.4 kV Dyn7 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.2 | 2.75 | 0.52 | 0.26001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
347 | 0fd3623beeff44fc97163d683f3b9a27 | 0.2 MVA 10/0.4 kV Dyn7 ASEA |  | No action |  | 10.0 | 0.4 | 0.2 | 2.75 | 0.69 | 0.34501 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
348 | a8222f183aa84495a643610babee1812 | 0.2 MVA 10/0.4 kV Dyn5 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.2 | 2.75 | 0.52 | 0.26001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
349 | f68acd3979fe445081094c3fd0bf75c4 | 0.2 MVA 10/0.4 kV Dyn5 ASEA |  | No action |  | 10.0 | 0.4 | 0.2 | 2.75 | 0.69 | 0.34501 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
350 | 72aff3379ed242a7aaba5439b57a3eb9 | 0.2 MVA 10/0.4 kV Dyn11 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.2 | 2.75 | 0.52 | 0.26001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
351 | e0ff1d0392a94b98a776b257f26abde2 | 0.2 MVA 10/0.4 kV Dyn11 ASEA |  | No action |  | 10.0 | 0.4 | 0.2 | 2.75 | 0.69 | 0.34501 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
352 | 21b0251f9cf044a08e18834af28b578c | 0.2 MVA 10/0.4 kV Dyn1 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.2 | 2.75 | 0.52 | 0.26001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
353 | 9b739a8cc892433983337dfc7ef138c2 | 0.2 MVA 10/0.4 kV Dyn1 ASEA |  | No action |  | 10.0 | 0.4 | 0.2 | 2.75 | 0.69 | 0.34501 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
354 | c972b36c17b245b49868c3a023ede8c0 | 0.2 MVA 10/0.4 kV DT 200/10 F SGB |  | No action |  | 10.0 | 0.4 | 0.2 | 2.3 | 0.65 | 0.32501 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
355 | 500c84aacc2f40338a187e38e3e5d32a | 0.2 MVA 10/0.4 kV DT 200 SGB |  | No action |  | 10.0 | 0.4 | 0.2 | 2.8 | 0.75 | 0.37501 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
356 | b7fbcd6dcf82413582421e0c4ab5012c | 0.2 MVA 10/0.4 kV DOTNL 200/10 SGB |  | No action |  | 10.0 | 0.4 | 0.2 | 3.6 | 0.355 | 0.17751 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
357 | 5daa7bfb208a47419017df8f13a36ab9 | 0.2 MVA 10/0.4 kV DOTN 200/10 SGB |  | No action |  | 10.0 | 0.4 | 0.2 | 3.6 | 0.445 | 0.22251 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
358 | 31d2c9f69bdf4821a4ef4d1c76577de1 | 0.2 MVA 10/0.4 kV DOTEL 200/10 SGB |  | No action |  | 10.0 | 0.4 | 0.2 | 2.85 | 0.36 | 0.18001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
359 | 794702cb30d74dde86e8cf641e3dd078 | 0.2 MVA 10/0.4 kV DOTE 200/10 SGB |  | No action |  | 10.0 | 0.4 | 0.2 | 2.85 | 0.55 | 0.27501 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
360 | 0e6fdb1b73184032b8e47245150d2250 | 0.2 MVA 10/0.4 kV 0.69 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.2 | 2.65 | 0.69 | 0.345 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
361 | 4b70dfc9be3e418e9144bbf4b58a1f4c | 0.2 MVA 10/0.4 kV 0.57 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.2 | 2.8 | 0.57 | 0.285 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
362 | d22d6c36f34545deab626462081190d8 | 0.2 MVA 10/0.4 kV 0.54 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.2 | 2.6 | 0.54 | 0.27 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
363 | dcd3fde9e9d24248a0d642ef3d88e763 | 0.2 MVA 10/0.4 kV 0.44 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.2 | 2.9 | 0.44 | 0.22 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
364 | 597d959f032e4a64add496a8f0fe4920 | 0.16 MVA 10/0.4 kV Yyn6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.16 | 2.3 | 0.46 | 0.28751 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
365 | e4e1db5f5ee742fa95664c5aab294d9b | 0.16 MVA 10/0.4 kV Yyn6 ASEA |  | No action |  | 10.0 | 0.4 | 0.16 | 2.3 | 0.61 | 0.38126 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
366 | 4af6af16df2842d5a9874ee8055e4c21 | 0.16 MVA 10/0.4 kV Yyn0 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.16 | 2.3 | 0.46 | 0.28751 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
367 | af892fef05994daea57d933ee4b9de4c | 0.16 MVA 10/0.4 kV Yyn0 ASEA |  | No action |  | 10.0 | 0.4 | 0.16 | 2.3 | 0.61 | 0.38126 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
368 | 0a3fbf83bd0743dea08bde46397125b1 | 0.16 MVA 10/0.4 kV Trafo Union wnr |  | No action |  | 10.0 | 0.4 | 0.16 | 2.5 | 0.45 | 0.28125 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
369 | 3b8dd6c58f4d48b5b27409f87a2c9a37 | 0.16 MVA 10/0.4 kV Trafo Union |  | No action |  | 10.0 | 0.4 | 0.16 | 2.4 | 0.55 | 0.34375 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
370 | 5ae61049fe804de6adc1ef32a412dd74 | 0.16 MVA 10/0.4 kV ET 160/23 SGB |  | No action |  | 10.0 | 0.4 | 0.16 | 2.1 | 0.58 | 0.36251 | 3.75 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
371 | 3662587ae091467f94c31985cb6c1b8f | 0.16 MVA 10/0.4 kV ET 160 SGB |  | No action |  | 10.0 | 0.4 | 0.16 | 2.1 | 0.58 | 0.36251 | 3.75 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
372 | 89afec90ea3745ca90ff61318d74a696 | 0.16 MVA 10/0.4 kV Dyn7 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.16 | 2.3 | 0.46 | 0.28751 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
373 | 58044b5e21934124ae8841310b1b11be | 0.16 MVA 10/0.4 kV Dyn7 ASEA |  | No action |  | 10.0 | 0.4 | 0.16 | 2.3 | 0.61 | 0.38126 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
374 | 9713f50cb28e41e1825ceb4778faa0da | 0.16 MVA 10/0.4 kV Dyn5 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.16 | 2.3 | 0.46 | 0.28751 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
375 | 5686ca403ece42b8ba8a2c6a0192a4b2 | 0.16 MVA 10/0.4 kV Dyn5 ASEA |  | No action |  | 10.0 | 0.4 | 0.16 | 2.3 | 0.61 | 0.38126 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
376 | 986880bad2b245c4a44173e241fb3502 | 0.16 MVA 10/0.4 kV Dyn11 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.16 | 2.3 | 0.46 | 0.28751 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
377 | cb7262abe7914d38826f8c4f3d57d7ff | 0.16 MVA 10/0.4 kV Dyn11 ASEA |  | No action |  | 10.0 | 0.4 | 0.16 | 2.3 | 0.61 | 0.38126 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
378 | 4772c535ae4d4c3aa0d68cb1fc106621 | 0.16 MVA 10/0.4 kV Dyn1 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.16 | 2.3 | 0.46 | 0.28751 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
379 | 9d86b174e9994c9b971a96b66c6529b7 | 0.16 MVA 10/0.4 kV Dyn1 ASEA |  | No action |  | 10.0 | 0.4 | 0.16 | 2.3 | 0.61 | 0.38126 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
380 | 35b13d24d0af4e8fb2fc10a14add358b | 0.16 MVA 10/0.4 kV DTTHL SGB |  | No action |  | 10.0 | 0.4 | 0.16 | 2.6 | 0.35 | 0.21876 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
381 | fce24e2ba11245259e06537968175114 | 0.16 MVA 10/0.4 kV DTKa 4 SGB |  | No action |  | 10.0 | 0.4 | 0.16 | 2.6 | 0.58 | 0.36251 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
382 | 088cfe387700412091d497882f1b760e | 0.16 MVA 10/0.4 kV DTKa 3.8 SGB |  | No action |  | 10.0 | 0.4 | 0.16 | 2.4 | 0.58 | 0.36251 | 3.8 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
383 | de7b705c4f5a412bb392e8523f9266bb | 0.16 MVA 10/0.4 kV DT 160/10 F SGB |  | No action |  | 10.0 | 0.4 | 0.16 | 2.3 | 0.65 | 0.40626 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
384 | 3314d12518734ed08d7ea27afc09be96 | 0.16 MVA 10/0.4 kV DT 160 SGB |  | No action |  | 10.0 | 0.4 | 0.16 | 2.3 | 0.63 | 0.39376 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
385 | 49758b24635845169399c58d05278f70 | 0.16 MVA 10/0.4 kV DOTNL 160/10 SGB |  | No action |  | 10.0 | 0.4 | 0.16 | 3.1 | 0.295 | 0.184385 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
386 | 3cc3b917be8e4282ac6c17b22a4ad57b | 0.16 MVA 10/0.4 kV DOTN 160/10 SGB |  | No action |  | 10.0 | 0.4 | 0.16 | 3.1 | 0.39 | 0.24376 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
387 | 04b645fd30be421795bfa372f72d8215 | 0.16 MVA 10/0.4 kV DOTEL 160/10 SGB |  | No action |  | 10.0 | 0.4 | 0.16 | 2.35 | 0.3 | 0.18751 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
388 | d8549b1f13414630bca6d8246e5d0e0d | 0.16 MVA 10/0.4 kV DOTE 160/10 SGB |  | No action |  | 10.0 | 0.4 | 0.16 | 2.35 | 0.46 | 0.28751 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
389 | 38f4d5ec237e49d3b46d18a46ac29817 | 0.16 MVA 10/0.4 kV 6 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.16 | 2.4 | 0.48 | 0.3 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
390 | 35d61e5381a14b4e88702aeab4fbf132 | 0.16 MVA 10/0.4 kV 4 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.16 | 2.3 | 0.48 | 0.3 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
391 | 428d3304896041f4ad52dca1ff16088a | 0.16 MVA 10/0.4 kV 0.61 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.16 | 2.3 | 0.61 | 0.38125 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
392 | a5423faafa6d45c486c72b2cc68f9c6a | 0.16 MVA 10/0.4 kV 0.37 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.16 | 2.4 | 0.37 | 0.23125 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
393 | abc134c69a7649b5852a2aadbc8f9876 | 0.125 MVA 10/0.4 kV Yyn6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.125 | 2.0 | 0.4 | 0.32001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
394 | 0b73aacbaf774f058f9749d800b98de4 | 0.125 MVA 10/0.4 kV Yyn6 ASEA |  | No action |  | 10.0 | 0.4 | 0.125 | 2.0 | 0.52 | 0.41601 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
395 | 9b009e54bc3e486283c53836892ffb17 | 0.125 MVA 10/0.4 kV Yyn0 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.125 | 2.0 | 0.4 | 0.32001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
396 | 88d3db2dc2e94db4acda85c16d0b5ec9 | 0.125 MVA 10/0.4 kV Yyn0 ASEA |  | No action |  | 10.0 | 0.4 | 0.125 | 2.0 | 0.52 | 0.41601 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
397 | 2ee3dcd6ed7143d99830f4b8103eb35b | 0.125 MVA 10/0.4 kV Trafo Union wnr |  | No action |  | 10.0 | 0.4 | 0.125 | 2.0 | 0.4 | 0.32001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
398 | 4e0160d5cf1f480894a5eab259ff5e12 | 0.125 MVA 10/0.4 kV Trafo Union |  | No action |  | 10.0 | 0.4 | 0.125 | 1.9 | 0.5 | 0.40001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
399 | f31e4ed69caf43ffb9732891af0156c6 | 0.125 MVA 10/0.4 kV Dyn7 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.125 | 2.0 | 0.4 | 0.32001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
400 | 69791303e33642f997b7cd5f47ffb76f | 0.125 MVA 10/0.4 kV Dyn7 ASEA |  | No action |  | 10.0 | 0.4 | 0.125 | 2.0 | 0.52 | 0.41601 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
401 | a3315325eca64948824d8727d8fa2f25 | 0.125 MVA 10/0.4 kV Dyn5 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.125 | 2.0 | 0.4 | 0.32001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
402 | 2fc4480b12c64b909b9834a07c87fb8e | 0.125 MVA 10/0.4 kV Dyn5 ASEA |  | No action |  | 10.0 | 0.4 | 0.125 | 2.0 | 0.52 | 0.41601 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
403 | 3c3aab98ba0d44e8ad964f826456f0d6 | 0.125 MVA 10/0.4 kV Dyn11 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.125 | 2.0 | 0.4 | 0.32001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
404 | afbc59bcb05e4fec9d6e08aba23a80c7 | 0.125 MVA 10/0.4 kV Dyn11 ASEA |  | No action |  | 10.0 | 0.4 | 0.125 | 2.0 | 0.52 | 0.41601 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
405 | 08b36c08fa27487998a30a36cf2bbeb7 | 0.125 MVA 10/0.4 kV Dyn1 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.125 | 2.0 | 0.4 | 0.32001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
406 | ff82a66b27ee494ebf513c95a0a4a96a | 0.125 MVA 10/0.4 kV Dyn1 ASEA |  | No action |  | 10.0 | 0.4 | 0.125 | 2.0 | 0.52 | 0.41601 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
407 | 9ba0d45f150846e68f480168681e2363 | 0.125 MVA 10/0.4 kV DOTNL 125/10 SGB |  | No action |  | 10.0 | 0.4 | 0.125 | 2.65 | 0.255 | 0.20401 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
408 | 29078769559a4cf6ab43fb7138787bdb | 0.125 MVA 10/0.4 kV DOTN 125/10 SGB |  | No action |  | 10.0 | 0.4 | 0.125 | 2.65 | 0.34 | 0.27201 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
409 | 73114b8ad793479a98597d2b048afb51 | 0.125 MVA 10/0.4 kV DOTEL 125/10 SGB |  | No action |  | 10.0 | 0.4 | 0.125 | 2.05 | 0.255 | 0.20401 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
410 | 64947b2a96ec4d9a95d140456f167a51 | 0.125 MVA 10/0.4 kV DOTE 125/10 SGB |  | No action |  | 10.0 | 0.4 | 0.125 | 2.05 | 0.39 | 0.31201 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
411 | 7aea232afce84509b85a16cad24a54d8 | 0.125 MVA 10/0.4 kV 0.52 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.125 | 1.9 | 0.52 | 0.416 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
412 | f1c9607f8cb04f278183580288ed7d90 | 0.125 MVA 10/0.4 kV 0.41 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.125 | 2.0 | 0.41 | 0.328 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
413 | 065d08800383443f951d5fca78afe82c | 0.125 MVA 10/0.4 kV 0.4 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.125 | 2.0 | 0.4 | 0.32 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
414 | 191ae3c6865b41a4a686ebc8a010f5ea | 0.125 MVA 10/0.4 kV 0.31 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.125 | 2.0 | 0.31 | 0.248 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
415 | e684d5ef15394474925d20d2412e9657 | 0.1 MVA 10/0.4 kV Yyn6 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.1 | 1.7 | 0.34 | 0.34001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
416 | 76b0538967a842a2a09f80660df5cd68 | 0.1 MVA 10/0.4 kV Yyn6 ASEA |  | No action |  | 10.0 | 0.4 | 0.1 | 1.7 | 0.44 | 0.44001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
417 | eaf6ed96a9f940208804edfcdb0a059c | 0.1 MVA 10/0.4 kV Yyn0 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.1 | 1.7 | 0.34 | 0.34001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
418 | bba5c4ca500e472eb8abd98ca2bb4907 | 0.1 MVA 10/0.4 kV Yyn0 ASEA |  | No action |  | 10.0 | 0.4 | 0.1 | 1.7 | 0.44 | 0.44001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
419 | 8c50e7b82ffb44c592321f4f0e721c29 | 0.1 MVA 10/0.4 kV Trafo Union wnr |  | No action |  | 10.0 | 0.4 | 0.1 | 1.9 | 0.35 | 0.35 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
420 | 413a99d5911945f78f9b40a7afc50f2c | 0.1 MVA 10/0.4 kV Trafo Union |  | No action |  | 10.0 | 0.4 | 0.1 | 1.9 | 0.45 | 0.45 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
421 | 3721482f5a324c22858c57e71af26df7 | 0.1 MVA 10/0.4 kV ET 100/23 SGB |  | No action |  | 10.0 | 0.4 | 0.1 | 1.5 | 0.42 | 0.42001 | 3.75 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
422 | 41d6daf7a0914e08b20eab66477865bf | 0.1 MVA 10/0.4 kV ET 100 SGB |  | No action |  | 10.0 | 0.4 | 0.1 | 1.5 | 0.42 | 0.42001 | 3.75 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
423 | 2a5e33dbdc2e49888c4c677aa06e3341 | 0.1 MVA 10/0.4 kV Dyn7 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.1 | 1.7 | 0.34 | 0.34001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
424 | 6d4f35ec5dc145b4960898a9ccbfee03 | 0.1 MVA 10/0.4 kV Dyn7 ASEA |  | No action |  | 10.0 | 0.4 | 0.1 | 1.7 | 0.44 | 0.44001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
425 | b1b3bbfdfe5e451a9c55d6c0ea111667 | 0.1 MVA 10/0.4 kV Dyn5 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.1 | 1.7 | 0.34 | 0.34001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
426 | d5afe4e656544e21a5fefb6297a68530 | 0.1 MVA 10/0.4 kV Dyn5 ASEA |  | No action |  | 10.0 | 0.4 | 0.1 | 1.7 | 0.44 | 0.44001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
427 | 4c6025ce9b4c4f8ca468dd121b544a98 | 0.1 MVA 10/0.4 kV Dyn11 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.1 | 1.7 | 0.34 | 0.34001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
428 | 7ba48429e9e0439da4e05c5741516def | 0.1 MVA 10/0.4 kV Dyn11 ASEA |  | No action |  | 10.0 | 0.4 | 0.1 | 1.7 | 0.44 | 0.44001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
429 | d8108e5d1db14aebadc99b034c52f6ac | 0.1 MVA 10/0.4 kV Dyn1 wnr ASEA |  | No action |  | 10.0 | 0.4 | 0.1 | 1.7 | 0.34 | 0.34001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
430 | 649ab23f2eec42b1a630f4f0158405f2 | 0.1 MVA 10/0.4 kV Dyn1 ASEA |  | No action |  | 10.0 | 0.4 | 0.1 | 1.7 | 0.44 | 0.44001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
431 | 8e349962ab5f48f289b9b9b179118c2f | 0.1 MVA 10/0.4 kV DTTHL SGB |  | No action |  | 10.0 | 0.4 | 0.1 | 2.1 | 0.27 | 0.27001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
432 | e54bb783b1d34c618d24f262f8d65545 | 0.1 MVA 10/0.4 kV DTKa 4 SGB |  | No action |  | 10.0 | 0.4 | 0.1 | 1.95 | 0.45 | 0.45001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
433 | c0b42dd313444872bef8d4e1dcd4a95b | 0.1 MVA 10/0.4 kV DTKa 3.8 SGB |  | No action |  | 10.0 | 0.4 | 0.1 | 1.85 | 0.45 | 0.45001 | 3.8 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
434 | 0c421278e04348008bf00e3cf4ef3522 | 0.1 MVA 10/0.4 kV DT 100/10 F SGB |  | No action |  | 10.0 | 0.4 | 0.1 | 1.7 | 0.51 | 0.51001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
435 | ba7695791e4c4aa7bb54e660e048e6e1 | 0.1 MVA 10/0.4 kV DT 100 SGB |  | No action |  | 10.0 | 0.4 | 0.1 | 1.7 | 0.44 | 0.44001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
436 | 9f979445ab304a73906b3d09cee9b9e8 | 0.1 MVA 10/0.4 kV DOTNL 100/10 SGB |  | No action |  | 10.0 | 0.4 | 0.1 | 2.15 | 0.21 | 0.21001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
437 | 25ec6dc6dcc543e4a9d5b28a7eee5242 | 0.1 MVA 10/0.4 kV DOTN 100/10 SGB |  | No action |  | 10.0 | 0.4 | 0.1 | 2.15 | 0.29 | 0.29001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
438 | 35c4dc7e6ee64a9caa1d0e29c33eb042 | 0.1 MVA 10/0.4 kV DOTEL 100/10 SGB |  | No action |  | 10.0 | 0.4 | 0.1 | 1.75 | 0.21 | 0.21001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
439 | 79a677bd809e47b8b06fe5b14f371f43 | 0.1 MVA 10/0.4 kV DOTE 100/10 SGB |  | No action |  | 10.0 | 0.4 | 0.1 | 1.75 | 0.32 | 0.32001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
440 | b696c49ed608432394e914e563a6909e | 0.1 MVA 10/0.4 kV 6 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.1 | 1.7 | 0.34 | 0.34 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
441 | 51f726a620674de0b7c97d64ce3eae4c | 0.1 MVA 10/0.4 kV 4 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.1 | 1.7 | 0.34 | 0.34 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
442 | ce4d79a4171e4af48d6dd44cd8dafe54 | 0.1 MVA 10/0.4 kV 0.44 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.1 | 1.6 | 0.44 | 0.44 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
443 | fb620689cc3a4f5fa0698159245122dc | 0.1 MVA 10/0.4 kV 0.27 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.1 | 1.7 | 0.27 | 0.27 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
444 | 26818c893b374d8a98fb152570b96583 | 0.075 MVA 10/0.4 kV 0.36 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.075 | 1.35 | 0.36 | 0.48 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
445 | 8e66e999bc00445b9eecfabae7c5aeaa | 0.075 MVA 10/0.4 kV 0.28 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.075 | 1.35 | 0.28 | 0.3733333 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
446 | f99f3c5a7b9f4662b8734cb73099af2d | 0.063 MVA 10/0.4 kV ET 63/23 SGB |  | No action |  | 10.0 | 0.4 | 0.063 | 1.05 | 0.3 | 0.4762 | 3.75 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
447 | 6981a66b6af04212950c9aca2e48b15c | 0.063 MVA 10/0.4 kV ET 63 SGB |  | No action |  | 10.0 | 0.4 | 0.063 | 1.05 | 0.3 | 0.4762 | 3.75 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
448 | 22e2cef88f214e8da730a0923abb5d2f | 0.063 MVA 10/0.4 kV DTKa 4 SGB |  | No action |  | 10.0 | 0.4 | 0.063 | 1.4 | 0.36 | 0.571439 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
449 | 1448b2c1f64b434cabed9ad889e2dd8c | 0.063 MVA 10/0.4 kV DTKa 3.8 SGB |  | No action |  | 10.0 | 0.4 | 0.063 | 1.4 | 0.36 | 0.571439 | 3.8 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
450 | ecd651eaeacd4272a92ce6f2f3e9142d | 0.063 MVA 10/0.4 kV DT 63/10 F SGB |  | No action |  | 10.0 | 0.4 | 0.063 | 1.35 | 0.42 | 0.666677 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
451 | e873020ab0b94588b18f49c2b338bd96 | 0.063 MVA 10/0.4 kV DT 63 SGB |  | No action |  | 10.0 | 0.4 | 0.063 | 1.2 | 0.33 | 0.52382 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
452 | fb83d2cd91824e3ab15ec1ae2a983f77 | 0.05 MVA 10/0.4 kV DTTHL SGB |  | No action |  | 10.0 | 0.4 | 0.05 | 1.3 | 0.18 | 0.36001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
453 | d3f0cdd5486a413ab74c8b0e426b7770 | 0.05 MVA 10/0.4 kV 0.28 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.05 | 1.0 | 0.28 | 0.56 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
454 | 1851e069c0914b148887214cc8a2201e | 0.05 MVA 10/0.4 kV 0.22 GEAFOL |  | No action |  | 10.0 | 0.4 | 0.05 | 1.05 | 0.22 | 0.44 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
455 | 3eddd021971e4e0b9cdb796a467b3961 | 0.04 MVA 10/0.4 kV ET 40/23 SGB |  | No action |  | 10.0 | 0.4 | 0.04 | 0.75 | 0.22 | 0.55001 | 3.75 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
456 | e5c0a299630d441fa9604e67172bffaa | 0.04 MVA 10/0.4 kV ET 40 SGB |  | No action |  | 10.0 | 0.4 | 0.04 | 0.75 | 0.22 | 0.55001 | 3.75 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
457 | 7cc9b4f697c242d0b1540a89605fa7b2 | 0.04 MVA 10/0.4 kV DT 40 SGB |  | No action |  | 10.0 | 0.4 | 0.04 | 0.9 | 0.27 | 0.67501 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
458 | db0da228de2c4e7f80d0b8346c017515 | 0.025 MVA 10/0.4 kV ET 25/23 SGB |  | No action |  | 10.0 | 0.4 | 0.025 | 0.55 | 0.15 | 0.60001 | 3.75 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
459 | 30d1669bb3d8461ea3a8242a6ded6349 | 0.025 MVA 10/0.4 kV ET 25 SGB |  | No action |  | 10.0 | 0.4 | 0.025 | 0.55 | 0.15 | 0.60001 | 3.75 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
460 | 0220ab15b19f4457ae15d3f3c7608ca4 | 0.025 MVA 10/0.4 kV DT 25 SGB |  | No action |  | 10.0 | 0.4 | 0.025 | 0.7 | 0.2 | 0.80001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
461 | fcbedc5cfe8843f4924accf56cb98750 | 0.016 MVA 10/0.4 kV ET 16/23 SGB |  | No action |  | 10.0 | 0.4 | 0.016 | 0.45 | 0.11 | 0.68751 | 3.75 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
462 | eac5fe017f834430838205fcd5750d1c | 0.016 MVA 10/0.4 kV ET 16 SGB |  | No action |  | 10.0 | 0.4 | 0.016 | 0.45 | 0.11 | 0.68751 | 3.75 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
463 | c8af4e03e894491795bac0cb7e22832b | 0.016 MVA 10/0.4 kV DT 16 SGB |  | No action |  | 10.0 | 0.4 | 0.016 | 0.45 | 0.15 | 0.93751 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
464 | bca04211a5134d918c819af14f530f1b | 0.01 MVA 10/0.4 kV DT 10 SGB |  | No action |  | 10.0 | 0.4 | 0.01 | 0.35 | 0.12 | 1.20001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
465 | 921f6271edb24880bd85e1a9d318c9ee | 0.05 MVA 20/0.4 kV DTTHL SGB |  | No action |  | 20.0 | 0.4 | 0.05 | 1.4 | 0.2 | 0.40001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
466 | 952e9789e0994ed49f2a063cb07dc439 | 0.05 MVA 20/0.4 kV DTTHXL SGB |  | No action |  | 20.0 | 0.4 | 0.05 | 1.3 | 0.275 | 0.55001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
467 | 9de3f5230fad45b7b3e20964f77cc6ae | 0.1 MVA 20/0.4 kV 0.37 GEAFOL |  | No action |  | 20.0 | 0.4 | 0.1 | 1.8 | 0.37 | 0.37 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
468 | 11febcaa55c04d1e804b4c6ac2177f1b | 0.1 MVA 20/0.4 kV 0.48 GEAFOL |  | No action |  | 20.0 | 0.4 | 0.1 | 1.8 | 0.48 | 0.48 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
469 | 439a526fafdc401480824e1685c51b4c | 0.1 MVA 20/0.4 kV DOTE 100/20 SGB |  | No action |  | 20.0 | 0.4 | 0.1 | 1.75 | 0.32 | 0.32001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
470 | ffa04af4d8dd4b948112001c83e4d10f | 0.1 MVA 20/0.4 kV DOTEL 100/20 SGB |  | No action |  | 20.0 | 0.4 | 0.1 | 1.75 | 0.21 | 0.21001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
471 | d18d18245b504ea58e421794989fa3f5 | 0.1 MVA 20/0.4 kV DOTN 100/20 SGB |  | No action |  | 20.0 | 0.4 | 0.1 | 2.15 | 0.305 | 0.30501 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
472 | 60c53d7a349044f39d3a27e5bc1f802c | 0.1 MVA 20/0.4 kV DOTNL 100/20 SGB |  | No action |  | 20.0 | 0.4 | 0.1 | 2.15 | 0.22 | 0.22001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
473 | fc990edf46b14ca6b707c479968c5e7c | 0.1 MVA 20/0.4 kV DTTHL SGB |  | No action |  | 20.0 | 0.4 | 0.1 | 2.3 | 0.3 | 0.30001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
474 | c4d94d0110f34b0b9b9a3f5c7932966a | 0.1 MVA 20/0.4 kV DTTHXL SGB |  | No action |  | 20.0 | 0.4 | 0.1 | 2.1 | 0.375 | 0.37501 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
475 | b5ca746e7e83495794823fc3d71b36d1 | 0.1 MVA 20/0.4 kV Trafo Union |  | No action |  | 20.0 | 0.4 | 0.1 | 2.1 | 0.53 | 0.53 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
476 | a8a6f530ea3b467393b6221831cc2902 | 0.1 MVA 20/0.4 kV Trafo Union wnr |  | No action |  | 20.0 | 0.4 | 0.1 | 2.1 | 0.4 | 0.4 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
477 | 7fe571e287e84b1b935354639567f009 | 0.125 MVA 20/0.4 kV 0.43 GEAFOL |  | No action |  | 20.0 | 0.4 | 0.125 | 2.15 | 0.43 | 0.344 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
478 | 2972d45177d741e3a3fcaec73a536f46 | 0.125 MVA 20/0.4 kV 0.55 GEAFOL |  | No action |  | 20.0 | 0.4 | 0.125 | 2.15 | 0.55 | 0.44 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
479 | 45eebaf44807489b8b6b5c56047006d9 | 0.125 MVA 20/0.4 kV DOTE 125/20 SGB |  | No action |  | 20.0 | 0.4 | 0.125 | 2.05 | 0.39 | 0.31201 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
480 | 102649b1eabe477180d1f8375cf91bf5 | 0.125 MVA 20/0.4 kV DOTEL 125/20 SGB |  | No action |  | 20.0 | 0.4 | 0.125 | 2.05 | 0.255 | 0.20401 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
481 | b00d92bccc914c6e900dd4a636afb503 | 0.125 MVA 20/0.4 kV DOTN 125/20 SGB |  | No action |  | 20.0 | 0.4 | 0.125 | 2.65 | 0.36 | 0.28801 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
482 | 93af76f9963e4e5dae2f0b5162b2d4bb | 0.125 MVA 20/0.4 kV DOTNL 125/20 SGB |  | No action |  | 20.0 | 0.4 | 0.125 | 2.65 | 0.265 | 0.21201 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
483 | dace9958113e45cfbfc254f7d99fd014 | 0.125 MVA 20/0.4 kV Trafo Union |  | No action |  | 20.0 | 0.4 | 0.125 | 2.3 | 0.57 | 0.45601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
484 | 06b73520c9934ee8a6d9d23dd9bba776 | 0.125 MVA 20/0.4 kV Trafo Union wnr |  | No action |  | 20.0 | 0.4 | 0.125 | 2.4 | 0.45 | 0.36001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
485 | 49cede2ded2848db96ce08abce3bc06b | 0.16 MVA 20/0.4 kV 0.51 GEAFOL |  | No action |  | 20.0 | 0.4 | 0.16 | 2.6 | 0.51 | 0.31875 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
486 | ca98eb12e2ba477192cf5c82f2635e77 | 0.16 MVA 20/0.4 kV 0.65 GEAFOL |  | No action |  | 20.0 | 0.4 | 0.16 | 2.6 | 0.65 | 0.40625 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
487 | 3114dbcb4bbb4a7bb73d8cbd9c8c2d07 | 0.16 MVA 20/0.4 kV DOTE 160/20 SGB |  | No action |  | 20.0 | 0.4 | 0.16 | 2.35 | 0.46 | 0.28751 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
488 | 62f016b2b8d748ecba95cdfae025647e | 0.16 MVA 20/0.4 kV DOTEL 160/20 SGB |  | No action |  | 20.0 | 0.4 | 0.16 | 2.35 | 0.3 | 0.18751 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
489 | a082fcf05e9048b6934e9067c8b23465 | 0.16 MVA 20/0.4 kV DOTN 160/20 SGB |  | No action |  | 20.0 | 0.4 | 0.16 | 3.1 | 0.41 | 0.25626 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
490 | 9b3ffac128c2433e8bde48b7457f5ba7 | 0.16 MVA 20/0.4 kV DOTNL 160/20 SGB |  | No action |  | 20.0 | 0.4 | 0.16 | 3.1 | 0.31 | 0.19376 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
491 | 285f7fcf0ed54637adbd9f32955e20e4 | 0.16 MVA 20/0.4 kV DTTHL SGB |  | No action |  | 20.0 | 0.4 | 0.16 | 2.9 | 0.39 | 0.24376 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
492 | 31e4664e8c33421391185b12aa661259 | 0.16 MVA 20/0.4 kV DTTHXL SGB |  | No action |  | 20.0 | 0.4 | 0.16 | 2.5 | 0.48 | 0.30001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
493 | 0e7acf4153164f81a8b598c80f17f35f | 0.16 MVA 20/0.4 kV Trafo Union |  | No action |  | 20.0 | 0.4 | 0.16 | 2.8 | 0.65 | 0.40625 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
494 | 2904148fd1174261ade6924ea667fb0b | 0.16 MVA 20/0.4 kV Trafo Union wnr |  | No action |  | 20.0 | 0.4 | 0.16 | 3.0 | 0.52 | 0.325 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
495 | 66872a35b7fe42fdbb135169a96c91a9 | 0.2 MVA 20/0.4 kV 0.59 GEAFOL |  | No action |  | 20.0 | 0.4 | 0.2 | 3.1 | 0.59 | 0.295 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
496 | 3137ad80aec446d19e54ae20904afc32 | 0.2 MVA 20/0.4 kV 0.75 GEAFOL |  | No action |  | 20.0 | 0.4 | 0.2 | 2.9 | 0.75 | 0.375 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
497 | b2f4880eb7fc4cac98917caf524ea3d0 | 0.2 MVA 20/0.4 kV DOTE 200/20 SGB |  | No action |  | 20.0 | 0.4 | 0.2 | 2.85 | 0.55 | 0.27501 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
498 | 7fe74c809c2a406eb19cfd13ff797043 | 0.2 MVA 20/0.4 kV DOTEL 200/20 SGB |  | No action |  | 20.0 | 0.4 | 0.2 | 2.85 | 0.36 | 0.18001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
499 | 508a8f4568b04cc1ae52968c55347fbc | 0.2 MVA 20/0.4 kV DOTN 200/20 SGB |  | No action |  | 20.0 | 0.4 | 0.2 | 3.6 | 0.465 | 0.23251 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
500 | b6d09852125f4546920dc62163b6f9e3 | 0.2 MVA 20/0.4 kV DOTNL 200/20 SGB |  | No action |  | 20.0 | 0.4 | 0.2 | 3.6 | 0.37 | 0.18501 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
501 | 304aac94653c4cf9a8fe019a48e07829 | 0.2 MVA 20/0.4 kV Trafo Union |  | No action |  | 20.0 | 0.4 | 0.2 | 3.0 | 0.73 | 0.365 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
502 | 1975be10ad2343a9af15eaab5717d0a3 | 0.2 MVA 20/0.4 kV Trafo Union wnr |  | No action |  | 20.0 | 0.4 | 0.2 | 3.1 | 0.63 | 0.31501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
503 | 36ab346ca1144f7dade2eb62f100cbb0 | 0.25 MVA 20/0.4 kV 0.45 Trafo Union |  | No action |  | 20.0 | 0.4 | 0.25 | 3.6 | 0.8 | 0.32001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
504 | bb0adbe7f27e4403b43079f849863e16 | 0.25 MVA 20/0.4 kV 0.57 Trafo Union wnr |  | No action |  | 20.0 | 0.4 | 0.25 | 3.7 | 0.67 | 0.26801 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
505 | 2a6d415e66a94428bb218bcbfb62f73b | 0.25 MVA 20/0.4 kV 0.67 Trafo Union |  | No action |  | 20.0 | 0.4 | 0.25 | 3.6 | 0.8 | 0.32001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
506 | 2c39f6582211461c9973138544806f33 | 0.25 MVA 20/0.4 kV 0.69 GEAFOL |  | No action |  | 20.0 | 0.4 | 0.25 | 3.3 | 0.69 | 0.276 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
507 | cc33bbb6398b44e388468ea96503a8de | 0.25 MVA 20/0.4 kV 0.8 Trafo Union wnr |  | No action |  | 20.0 | 0.4 | 0.25 | 3.7 | 0.67 | 0.26801 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
508 | 0f5cac74205c4639ae3889d7cafe3bb8 | 0.25 MVA 20/0.4 kV 0.88 GEAFOL |  | No action |  | 20.0 | 0.4 | 0.25 | 3.3 | 0.88 | 0.352 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
509 | ea04b86ca6e7420fa599ff250f082968 | 0.25 MVA 20/0.4 kV DOTE 250/20 SGB |  | No action |  | 20.0 | 0.4 | 0.25 | 3.25 | 0.65 | 0.26001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
510 | d16eb40faa20415593cf0083e9d32352 | 0.25 MVA 20/0.4 kV DOTEL 250/20 SGB |  | No action |  | 20.0 | 0.4 | 0.25 | 3.25 | 0.42 | 0.16801 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
511 | a977b8d1ecdb471f9cccf04a6b6ca401 | 0.25 MVA 20/0.4 kV DOTN 250/20 SGB |  | No action |  | 20.0 | 0.4 | 0.25 | 4.1 | 0.57 | 0.22801 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
512 | 43c5945ef36c491cb7eddc522d1caf9b | 0.25 MVA 20/0.4 kV DOTNL 250/20 SGB |  | No action |  | 20.0 | 0.4 | 0.25 | 4.1 | 0.435 | 0.17401 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
513 | bc3870930f7a4e1cbd46b29cf15f5e3c | 0.25 MVA 20/0.4 kV DTTHL SGB |  | No action |  | 20.0 | 0.4 | 0.25 | 3.5 | 0.55 | 0.22001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
514 | 5c1c806d6a3f4d599407871b63f5e03d | 0.25 MVA 20/0.4 kV DTTHXL SGB |  | No action |  | 20.0 | 0.4 | 0.25 | 3.0 | 0.65 | 0.26001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
515 | 61edf19834ac4a3da16b7f8fbe898ebb | 0.25 MVA 20/0.4 kV Dyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.25 | 3.3 | 0.67 | 0.26801 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
516 | d630dfa8470347ef9209787dc42f3e2a | 0.25 MVA 20/0.4 kV Dyn1 ASEA |  | No action |  | 20.0 | 0.4 | 0.25 | 3.3 | 0.88 | 0.35201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
517 | cd43956b855b4d158a2de347b7fdaf87 | 0.25 MVA 20/0.4 kV Dyn1 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.25 | 3.3 | 0.67 | 0.26801 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
518 | c0cebb6e717a42beaa2998d7b4166c4e | 0.25 MVA 20/0.4 kV Dyn11 ASEA |  | No action |  | 20.0 | 0.4 | 0.25 | 3.3 | 0.88 | 0.35201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
519 | 2a6bac9d414142b8aed65f499fbaf93b | 0.25 MVA 20/0.4 kV Dyn11 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.25 | 3.3 | 0.67 | 0.26801 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
520 | da39d997bae44825bb8ef54491e22f01 | 0.25 MVA 20/0.4 kV Dyn5 ASEA |  | No action |  | 20.0 | 0.4 | 0.25 | 3.3 | 0.88 | 0.35201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
521 | c2216df5efc34baa9646141aaf855041 | 0.25 MVA 20/0.4 kV Dyn7 ASEA |  | No action |  | 20.0 | 0.4 | 0.25 | 3.3 | 0.88 | 0.35201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
522 | 3effcae75fb148079e8e80b1bf80a26d | 0.25 MVA 20/0.4 kV Dyn7 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.25 | 3.3 | 0.67 | 0.26801 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
523 | d8296456bcd84dd981d9867fe9439e6c | 0.25 MVA 20/0.4 kV Yyn0 ASEA |  | No action |  | 20.0 | 0.4 | 0.25 | 3.3 | 0.88 | 0.35201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
524 | df1736a641274e83b6eb845258723f33 | 0.25 MVA 20/0.4 kV Yyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.25 | 3.3 | 0.67 | 0.26801 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
525 | c672558daaba40eaae83970ab207b15d | 0.25 MVA 20/0.4 kV Yyn6 ASEA |  | No action |  | 20.0 | 0.4 | 0.25 | 3.3 | 0.88 | 0.35201 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
526 | d8edc80fbd0b4476ac5944d0ecdc092a | 0.25 MVA 20/0.4 kV Yyn6 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.25 | 3.3 | 0.67 | 0.26801 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
527 | 284e013d621e44a799eceba39ac2b56d | 0.315 MVA 20/0.4 kV 0.82 GEAFOL |  | No action |  | 20.0 | 0.4 | 0.315 | 4.0 | 0.82 | 0.2603175 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
528 | 9bcdfd8aedf0474299dbd9e722e3d262 | 0.315 MVA 20/0.4 kV 1.05 GEAFOL |  | No action |  | 20.0 | 0.4 | 0.315 | 4.0 | 1.05 | 0.3333333 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
529 | 0c277670860c40f697db2151cdb00cc3 | 0.315 MVA 20/0.4 kV DOTE 315/20 SGB |  | No action |  | 20.0 | 0.4 | 0.315 | 3.9 | 0.77 | 0.244454 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
530 | 97c8fd1b611040ccbb3a0e384db93449 | 0.315 MVA 20/0.4 kV DOTEL 315/20 SGB |  | No action |  | 20.0 | 0.4 | 0.315 | 3.9 | 0.5 | 0.15874 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
531 | 979fd13640c34d8db26d1d82bd91c68f | 0.315 MVA 20/0.4 kV DOTN 315/20 SGB |  | No action |  | 20.0 | 0.4 | 0.315 | 4.9 | 0.68 | 0.215883 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
532 | 0a97eaf3a4054e2da0b7093ca9523a8b | 0.315 MVA 20/0.4 kV DOTNL 315/20 SGB |  | No action |  | 20.0 | 0.4 | 0.315 | 4.9 | 0.52 | 0.165089 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
533 | f3616c60676c4c18a2eb74a4cdc72442 | 0.315 MVA 20/0.4 kV Dyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.315 | 4.0 | 0.82 | 0.260327 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
534 | e67c08ff654b40c096cb2fad906b34d0 | 0.315 MVA 20/0.4 kV Dyn1 ASEA |  | No action |  | 20.0 | 0.4 | 0.315 | 4.0 | 1.05 | 0.333343 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
535 | 302b5c06a4524620b422350365d5185c | 0.315 MVA 20/0.4 kV Dyn1 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.315 | 4.0 | 0.82 | 0.260327 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
536 | 3660c0b15dd04c709c364faa420634e6 | 0.315 MVA 20/0.4 kV Dyn11 ASEA |  | No action |  | 20.0 | 0.4 | 0.315 | 4.0 | 1.05 | 0.333343 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
537 | da0682d3ae514f6eb5d98ed6f63a01ad | 0.315 MVA 20/0.4 kV Dyn11 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.315 | 4.0 | 0.82 | 0.260327 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
538 | 6f665e455c934afa8180ee6d669413fd | 0.315 MVA 20/0.4 kV Dyn5 ASEA |  | No action |  | 20.0 | 0.4 | 0.315 | 4.0 | 1.05 | 0.333343 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
539 | 0a41beae281449ca8f7d09ae286eedbb | 0.315 MVA 20/0.4 kV Dyn7 ASEA |  | No action |  | 20.0 | 0.4 | 0.315 | 4.0 | 1.05 | 0.333343 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
540 | f420be63d88b43dc8c702cf91656deeb | 0.315 MVA 20/0.4 kV Dyn7 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.315 | 4.0 | 0.82 | 0.260327 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
541 | a06fad41c15e45b49334fac4938999f2 | 0.315 MVA 20/0.4 kV Trafo Union |  | No action |  | 20.0 | 0.4 | 0.315 | 4.5 | 1.23 | 0.3904762 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
542 | 6cb86599e776452c950e0f18056a5b58 | 0.315 MVA 20/0.4 kV Trafo Union wnr |  | No action |  | 20.0 | 0.4 | 0.315 | 4.7 | 0.95 | 0.3015873 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
543 | db94df8ec08341f9bcced79019e36c16 | 0.315 MVA 20/0.4 kV Yyn0 ASEA |  | No action |  | 20.0 | 0.4 | 0.315 | 4.0 | 1.05 | 0.333343 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
544 | 3b2e508db3a24814bebbcb12fd6e5a8f | 0.315 MVA 20/0.4 kV Yyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.315 | 4.0 | 0.82 | 0.260327 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
545 | e0358f520b3b4e4698fdc4eb91d13082 | 0.315 MVA 20/0.4 kV Yyn6 ASEA |  | No action |  | 20.0 | 0.4 | 0.315 | 4.0 | 1.05 | 0.333343 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
546 | 9658dfacfae94c3686029d5b4df63892 | 0.315 MVA 20/0.4 kV Yyn6 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.315 | 4.0 | 0.82 | 0.260327 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
547 | fb1bf4f0284140fab0e4e96d55d90e42 | 0.4 MVA 20/0.4 kV 0.94 GEAFOL |  | No action |  | 20.0 | 0.4 | 0.4 | 4.8 | 0.94 | 0.235 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
548 | 847f9ac5009b4cfabab7e85fa6e97c66 | 0.4 MVA 20/0.4 kV 1.2 GEAFOL |  | No action |  | 20.0 | 0.4 | 0.4 | 4.8 | 1.2 | 0.3 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
549 | d2bcc9004ff54bb9a92a66678ef2dbeb | 0.4 MVA 20/0.4 kV 1.2 GEAFOL/FC |  | No action |  | 20.0 | 0.4 | 0.4 | 4.5 | 1.2 | 0.3 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
550 | 24a4402b1ac64a2484a6ab8689cd559b | 0.4 MVA 20/0.4 kV DOTE 400/20 SGB |  | No action |  | 20.0 | 0.4 | 0.4 | 4.6 | 0.93 | 0.23251 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
551 | a501e50352aa4b52a108b0de79bfd8f9 | 0.4 MVA 20/0.4 kV DOTEL 400/20 SGB |  | No action |  | 20.0 | 0.4 | 0.4 | 4.6 | 0.6 | 0.15001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
552 | ff78ad0bc09c47b58e8b148a9f62e0b7 | 0.4 MVA 20/0.4 kV DOTN 400/20 SGB |  | No action |  | 20.0 | 0.4 | 0.4 | 6.0 | 0.815 | 0.20376 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
553 | 50a18966938443d6bb126f3904ef7268 | 0.4 MVA 20/0.4 kV DOTNL 400/20 SGB |  | No action |  | 20.0 | 0.4 | 0.4 | 6.0 | 0.625 | 0.15626 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
554 | 28cd490dd4d24e3aa4b80cf0b70459ba | 0.4 MVA 20/0.4 kV DTTH SGB |  | No action |  | 20.0 | 0.4 | 0.4 | 4.8 | 1.1 | 0.27501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
555 | 2b97a10bdab34c28ae239422f75564c7 | 0.4 MVA 20/0.4 kV DTTHL SGB |  | No action |  | 20.0 | 0.4 | 0.4 | 4.8 | 0.87 | 0.21751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
556 | f39c24e4b58d4ee69906d4fdee189caa | 0.4 MVA 20/0.4 kV DTTHXL SGB |  | No action |  | 20.0 | 0.4 | 0.4 | 4.8 | 0.9 | 0.22501 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
557 | 168568a737084b60a49023f149eabbc3 | 0.4 MVA 20/0.4 kV Dyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.4 | 4.8 | 0.94 | 0.23501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
558 | 8d1a1f57468b48ee953a70f74cf61ae6 | 0.4 MVA 20/0.4 kV Dyn1 ASEA |  | No action |  | 20.0 | 0.4 | 0.4 | 4.8 | 1.2 | 0.30001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
559 | cacdf7af72f741eda4534ba76f92c384 | 0.4 MVA 20/0.4 kV Dyn1 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.4 | 4.8 | 0.94 | 0.23501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
560 | 8228b061900b46a2a3b0c092bba97f0f | 0.4 MVA 20/0.4 kV Dyn11 ASEA |  | No action |  | 20.0 | 0.4 | 0.4 | 4.8 | 1.2 | 0.30001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
561 | a08c9681cbb7491890352a23148fa25d | 0.4 MVA 20/0.4 kV Dyn11 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.4 | 4.8 | 0.94 | 0.23501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
562 | c032beb58d084476aee9a98505902713 | 0.4 MVA 20/0.4 kV Dyn5 ASEA |  | No action |  | 20.0 | 0.4 | 0.4 | 4.8 | 1.2 | 0.30001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
563 | aa842dca72fd45c4a2cdddcfb2d4d3f9 | 0.4 MVA 20/0.4 kV Dyn7 ASEA |  | No action |  | 20.0 | 0.4 | 0.4 | 4.8 | 1.2 | 0.30001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
564 | fe6f25f195464467bd07eeca23d2b09b | 0.4 MVA 20/0.4 kV Dyn7 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.4 | 4.8 | 0.94 | 0.23501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
565 | 1a4f917478594c57b312f18bc3868369 | 0.4 MVA 20/0.4 kV Trafo Union |  | No action |  | 20.0 | 0.4 | 0.4 | 5.7 | 1.35 | 0.3375 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
566 | 6159c8b0b24c4b68b74874def327636a | 0.4 MVA 20/0.4 kV Trafo Union wnr |  | No action |  | 20.0 | 0.4 | 0.4 | 5.5 | 1.05 | 0.2625 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
567 | 1614a3b19cd540168d70d3fd6363c001 | 0.4 MVA 20/0.4 kV Yyn0 ASEA |  | No action |  | 20.0 | 0.4 | 0.4 | 4.8 | 1.2 | 0.30001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
568 | 8c54f1b860354f96bbf1e68af54428eb | 0.4 MVA 20/0.4 kV Yyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.4 | 4.8 | 0.94 | 0.23501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
569 | de2a93fa7f7f49e991776b76be9a6d10 | 0.4 MVA 20/0.4 kV Yyn6 ASEA |  | No action |  | 20.0 | 0.4 | 0.4 | 4.8 | 1.2 | 0.30001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
570 | d68764c9a72a4884b33b557f8837b80c | 0.4 MVA 20/0.4 kV Yyn6 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.4 | 4.8 | 0.94 | 0.23501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
571 | 8f4ed74464e7477c88b098dda0a0dae5 | 0.5 MVA 20/0.4 kV 1.09 GEAFOL |  | No action |  | 20.0 | 0.4 | 0.5 | 5.7 | 1.09 | 0.218 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
572 | ff7439a91421464bbfdffafcb0458d7d | 0.5 MVA 20/0.4 kV 1.4 GEAFOL |  | No action |  | 20.0 | 0.4 | 0.5 | 5.0 | 1.4 | 0.28 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
573 | c1a896f00d37442688089e209b443953 | 0.5 MVA 20/0.4 kV 1.4 GEAFOL/FC |  | No action |  | 20.0 | 0.4 | 0.5 | 5.4 | 1.4 | 0.28 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
574 | 990d45955c1e45b2b1e86e7889209903 | 0.5 MVA 20/0.4 kV DOTE 500/20 SGB |  | No action |  | 20.0 | 0.4 | 0.5 | 5.5 | 1.1 | 0.22001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
575 | 41a32985dc8949d8969df9364c3553f5 | 0.5 MVA 20/0.4 kV DOTEL 500/20 SGB |  | No action |  | 20.0 | 0.4 | 0.5 | 5.5 | 0.72 | 0.14401 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
576 | 36ab50db7fae4650bfc92c0743f0fdbb | 0.5 MVA 20/0.4 kV DOTN 500/20 SGB |  | No action |  | 20.0 | 0.4 | 0.5 | 7.15 | 0.98 | 0.19601 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
577 | 489046c665d349d59909bd73302473fb | 0.5 MVA 20/0.4 kV DOTNL 500/20 SGB |  | No action |  | 20.0 | 0.4 | 0.5 | 7.15 | 0.75 | 0.15001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
578 | 1107b12bd7e34fa18430a865f29f1ebe | 0.5 MVA 20/0.4 kV DTTH SGB |  | No action |  | 20.0 | 0.4 | 0.5 | 6.0 | 1.2 | 0.24001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
579 | 1ce70558e6e647c6b96deafda4ce87ed | 0.5 MVA 20/0.4 kV DTTHL SGB |  | No action |  | 20.0 | 0.4 | 0.5 | 6.0 | 0.95 | 0.19001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
580 | 544f62793e974a15a62bbab0876ed325 | 0.5 MVA 20/0.4 kV DTTHXL SGB |  | No action |  | 20.0 | 0.4 | 0.5 | 5.1 | 1.15 | 0.23001 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
581 | 4a28c908b1db4d978f584caf05d2bd74 | 0.5 MVA 20/0.4 kV Dyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.5 | 6.0 | 1.1 | 0.22001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
582 | 7718bc9f65a6452f87cc484533a2eab7 | 0.5 MVA 20/0.4 kV Dyn1 ASEA |  | No action |  | 20.0 | 0.4 | 0.5 | 6.0 | 1.4 | 0.28001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
583 | cd385e0efe904518b021cfd75d2e9af9 | 0.5 MVA 20/0.4 kV Dyn1 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.5 | 6.0 | 1.1 | 0.22001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
584 | b0706df81c0d4bb8bc06f71f7d160175 | 0.5 MVA 20/0.4 kV Dyn11 ASEA |  | No action |  | 20.0 | 0.4 | 0.5 | 6.0 | 1.4 | 0.28001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
585 | 23627f175fbe40e895c56e37bb947a12 | 0.5 MVA 20/0.4 kV Dyn11 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.5 | 6.0 | 1.1 | 0.22001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
586 | 281334f5d5294ad69f677d607590b9e4 | 0.5 MVA 20/0.4 kV Dyn5 ASEA |  | No action |  | 20.0 | 0.4 | 0.5 | 6.0 | 1.4 | 0.28001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
587 | f2ea28d0a314460eaef94c15ba838591 | 0.5 MVA 20/0.4 kV Dyn7 ASEA |  | No action |  | 20.0 | 0.4 | 0.5 | 6.0 | 1.4 | 0.28001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
588 | 12e500619b2349af98870f36cfa4e14a | 0.5 MVA 20/0.4 kV Dyn7 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.5 | 6.0 | 1.1 | 0.22001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
589 | f2ac3b6d500d44cc89a27446bde58d7f | 0.5 MVA 20/0.4 kV Trafo Union |  | No action |  | 20.0 | 0.4 | 0.5 | 6.0 | 1.5 | 0.3 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
590 | 36f0fe81ada44a219641f06864b839ca | 0.5 MVA 20/0.4 kV Trafo Union wnr |  | No action |  | 20.0 | 0.4 | 0.5 | 6.4 | 1.17 | 0.234 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
591 | f1b0e37e1f4345d597e9a7adde322ed1 | 0.5 MVA 20/0.4 kV Yyn0 ASEA |  | No action |  | 20.0 | 0.4 | 0.5 | 6.0 | 1.4 | 0.28001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
592 | b429bedb211a413d8cd6b84e9e969593 | 0.5 MVA 20/0.4 kV Yyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.5 | 6.0 | 1.1 | 0.22001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
593 | 3d6335c746d94c028c55f211bfa4f8ac | 0.5 MVA 20/0.4 kV Yyn6 ASEA |  | No action |  | 20.0 | 0.4 | 0.5 | 6.0 | 1.4 | 0.28001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
594 | 2ee53041d39c4493bed56147d3ac525b | 0.5 MVA 20/0.4 kV Yyn6 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.5 | 6.0 | 1.1 | 0.22001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
595 | 464ccc6b03234f73b3ce44d8e658c550 | 0.63 MVA 20/0.4 kV 1.29 GEAFOL |  | No action |  | 20.0 | 0.4 | 0.63 | 6.6 | 1.29 | 0.2047619 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
596 | 30e31612df024fdca672f171d73dfddb | 0.63 MVA 20/0.4 kV 1.65 GEAFOL |  | No action |  | 20.0 | 0.4 | 0.63 | 6.9 | 1.65 | 0.2619048 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
597 | 7f4756c1a86a41a4b6764cf03347370c | 0.63 MVA 20/0.4 kV 1.65 GEAFOL/FC |  | No action |  | 20.0 | 0.4 | 0.63 | 6.4 | 1.65 | 0.2619048 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
598 | 89f3dc19433849779c1c59840fb21b5c | 0.63 MVA 20/0.4 kV DOTE 630/20 SGB |  | No action |  | 20.0 | 0.4 | 0.63 | 6.5 | 1.3 | 0.206359 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
599 | 8fe58ac4cd6646178ce8113e37242b9a | 0.63 MVA 20/0.4 kV DOTEL 630/20 SGB |  | No action |  | 20.0 | 0.4 | 0.63 | 6.5 | 0.85 | 0.134931 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
600 | 17f6d793a2a644278ee1e04df048609e | 0.63 MVA 20/0.4 kV DOTN 630/20 SGB |  | No action |  | 20.0 | 0.4 | 0.63 | 8.4 | 1.15 | 0.18255 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
601 | 2d080cd1d00a497abddb5a6b4354df23 | 0.63 MVA 20/0.4 kV DOTNL 630/20 SGB |  | No action |  | 20.0 | 0.4 | 0.63 | 8.4 | 0.88 | 0.139693 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
602 | 900ceca640404906b2d3a46a8ab36a93 | 0.63 MVA 20/0.4 kV DTTH SGB |  | No action |  | 20.0 | 0.4 | 0.63 | 6.9 | 1.38 | 0.219058 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
603 | a36f9b536bcb4683878fc13c010afaa4 | 0.63 MVA 20/0.4 kV DTTHL SGB |  | No action |  | 20.0 | 0.4 | 0.63 | 6.9 | 1.1 | 0.174613 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
604 | 5605a348be424c4cb1e5b19eb0de276e | 0.63 MVA 20/0.4 kV DTTHXL SGB |  | No action |  | 20.0 | 0.4 | 0.63 | 6.3 | 1.25 | 0.198423 | 4.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
605 | 06d4cae0457f483c8a3eb2676476502e | 0.63 MVA 20/0.4 kV Dyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.63 | 6.9 | 1.27 | 0.201597 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
606 | 72ad45b9219f4f2a8da3193efb40f730 | 0.63 MVA 20/0.4 kV Dyn1 ASEA |  | No action |  | 20.0 | 0.4 | 0.63 | 6.9 | 1.65 | 0.261915 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
607 | 7d00abbc5edb46b6aaf10906eb95e404 | 0.63 MVA 20/0.4 kV Dyn1 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.63 | 6.9 | 1.27 | 0.201597 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
608 | 2d16158e048a4152a6f1edbda0dbc395 | 0.63 MVA 20/0.4 kV Dyn11 ASEA |  | No action |  | 20.0 | 0.4 | 0.63 | 6.9 | 1.65 | 0.261915 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
609 | e9f506f2b8e249f6a74f6fbfa70c6cb3 | 0.63 MVA 20/0.4 kV Dyn11 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.63 | 6.9 | 1.27 | 0.201597 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
610 | f247be4264d243e6838e0665d000eb13 | 0.63 MVA 20/0.4 kV Dyn5 ASEA |  | No action |  | 20.0 | 0.4 | 0.63 | 6.9 | 1.65 | 0.261915 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
611 | 081dfa01143f491ab928f963e6511e27 | 0.63 MVA 20/0.4 kV Dyn7 ASEA |  | No action |  | 20.0 | 0.4 | 0.63 | 6.9 | 1.65 | 0.261915 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
612 | 4a7dae0f841c4028af1381d692362255 | 0.63 MVA 20/0.4 kV Dyn7 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.63 | 6.9 | 1.27 | 0.201597 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
613 | 9c5c1abc18764ba6ae53cc12d38f7575 | 0.63 MVA 20/0.4 kV Trafo Union |  | No action |  | 20.0 | 0.4 | 0.63 | 7.6 | 1.65 | 0.2619048 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
614 | b2f3989237a741c6a7cbaf68b0eb5c64 | 0.63 MVA 20/0.4 kV Trafo Union wnr |  | No action |  | 20.0 | 0.4 | 0.63 | 8.1 | 1.27 | 0.2015873 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
615 | 48b1acc1dc994d97a0b94d63237827f1 | 0.63 MVA 20/0.4 kV Yyn0 ASEA |  | No action |  | 20.0 | 0.4 | 0.63 | 6.9 | 1.65 | 0.261915 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
616 | d42a820401a84f74b2e0aa37ed30deb1 | 0.63 MVA 20/0.4 kV Yyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.63 | 6.9 | 1.27 | 0.201597 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
617 | bad650c577944dea84710bc9f441d077 | 0.63 MVA 20/0.4 kV Yyn6 ASEA |  | No action |  | 20.0 | 0.4 | 0.63 | 6.9 | 1.65 | 0.261915 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
618 | b68f59d3198a46028b56d55d42c106f0 | 0.63 MVA 20/0.4 kV Yyn6 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.63 | 6.9 | 1.27 | 0.201597 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
619 | 4455f53f1f624bb59e24093b5596a200 | 0.8 MVA 20/0.4 kV 1.48 GEAFOL |  | No action |  | 20.0 | 0.4 | 0.8 | 8.0 | 1.48 | 0.185 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
620 | 2946fbfb87794cd2b62935849e58873a | 0.8 MVA 20/0.4 kV 1.9 GEAFOL |  | No action |  | 20.0 | 0.4 | 0.8 | 8.0 | 1.9 | 0.2375 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
621 | aae4c13bdb2c4e77a20458e19cf438a3 | 0.8 MVA 20/0.4 kV 1.9 GEAFOL/FC |  | No action |  | 20.0 | 0.4 | 0.8 | 7.5 | 1.9 | 0.2375 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
622 | 10c6d1b8a689460cb4e1de7fbeadf21d | 0.8 MVA 20/0.4 kV DOTE 800/20 SGB |  | No action |  | 20.0 | 0.4 | 0.8 | 8.5 | 1.5 | 0.18751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
623 | 6f587d644ee24a39a1673fb7bda0bcd1 | 0.8 MVA 20/0.4 kV DOTEL 800/20 SGB |  | No action |  | 20.0 | 0.4 | 0.8 | 8.5 | 0.98 | 0.12251 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
624 | 075592b7408843f68d2829827fa25845 | 0.8 MVA 20/0.4 kV DTTH SGB |  | No action |  | 20.0 | 0.4 | 0.8 | 7.7 | 1.85 | 0.23126 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
625 | 97454811b11146e1896afeb025667fbf | 0.8 MVA 20/0.4 kV DTTHIL SGB |  | No action |  | 20.0 | 0.4 | 0.8 | 5.3 | 1.6 | 0.20001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
626 | 044339010531416a80d2a49acaccbf76 | 0.8 MVA 20/0.4 kV DTTHL SGB |  | No action |  | 20.0 | 0.4 | 0.8 | 7.5 | 1.4 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
627 | 1c4e514aeec74d408db40281f5ce79a9 | 0.8 MVA 20/0.4 kV Dyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.8 | 8.1 | 1.46 | 0.18251 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
628 | d507219d5c2243c68ef9e41e84546f48 | 0.8 MVA 20/0.4 kV Dyn1 ASEA |  | No action |  | 20.0 | 0.4 | 0.8 | 8.1 | 1.9 | 0.23751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
629 | 228a39ad0d574942a6b9df986cd47b2f | 0.8 MVA 20/0.4 kV Dyn1 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.8 | 8.1 | 1.46 | 0.18251 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
630 | ed23fe1b69774f49b8624bd67d9c9dbe | 0.8 MVA 20/0.4 kV Dyn11 ASEA |  | No action |  | 20.0 | 0.4 | 0.8 | 8.1 | 1.9 | 0.23751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
631 | 82a3ec5195cb498f9b7300285d367813 | 0.8 MVA 20/0.4 kV Dyn11 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.8 | 8.1 | 1.46 | 0.18251 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
632 | 01a0ca08a0f94fe8b087e2cf63178470 | 0.8 MVA 20/0.4 kV Dyn5 ASEA |  | No action |  | 20.0 | 0.4 | 0.8 | 8.1 | 1.9 | 0.23751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
633 | b87a4661d8b9423c83be7c8283186f6a | 0.8 MVA 20/0.4 kV Dyn7 ASEA |  | No action |  | 20.0 | 0.4 | 0.8 | 8.1 | 1.9 | 0.23751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
634 | 8fb1f71c5bee4428aac53d43d9ab3af3 | 0.8 MVA 20/0.4 kV Dyn7 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.8 | 8.1 | 1.46 | 0.18251 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
635 | 6d84d110330747c8a70b501a04689eff | 0.8 MVA 20/0.4 kV Trafo Union |  | No action |  | 20.0 | 0.4 | 0.8 | 7.4 | 1.8 | 0.225 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
636 | e455d86030f04b56a285d140caa5c3bf | 0.8 MVA 20/0.4 kV Trafo Union wnr |  | No action |  | 20.0 | 0.4 | 0.8 | 7.6 | 1.63 | 0.20375 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
637 | 21fe405df2bd4b9d81066df9c2d10a42 | 0.8 MVA 20/0.4 kV Yyn0 ASEA |  | No action |  | 20.0 | 0.4 | 0.8 | 8.1 | 1.9 | 0.23751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
638 | d7d01c0124164dee82c08805f853a580 | 0.8 MVA 20/0.4 kV Yyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.8 | 8.1 | 1.46 | 0.18251 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
639 | eb398ad0a5294ee1ba7546e728dd7b9e | 0.8 MVA 20/0.4 kV Yyn6 ASEA |  | No action |  | 20.0 | 0.4 | 0.8 | 8.1 | 1.9 | 0.23751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
640 | d124513a719d45c4b2defcd2bb34fe2a | 0.8 MVA 20/0.4 kV Yyn6 wnr ASEA |  | No action |  | 20.0 | 0.4 | 0.8 | 8.1 | 1.46 | 0.18251 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
641 | f2a257d2f3244516b1305077d3b59003 | 1 MVA 20/0.4 kV 1.79 GEAFOL |  | No action |  | 20.0 | 0.4 | 1.0 | 9.6 | 1.79 | 0.179 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
642 | 8adcd47a65a64bd088b2a3ec94a8301c | 1 MVA 20/0.4 kV 2.3 GEAFOL |  | No action |  | 20.0 | 0.4 | 1.0 | 8.9 | 2.3 | 0.23 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
643 | 09a97f9091944468bd28d5fd2539f2e7 | 1 MVA 20/0.4 kV 2.3 GEAFOL/FC |  | No action |  | 20.0 | 0.4 | 1.0 | 8.8 | 2.3 | 0.23 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
644 | a5b9cb939b684fa1891a09f2869939b0 | 1 MVA 20/0.4 kV DOTE 1000/20 SGB |  | No action |  | 20.0 | 0.4 | 1.0 | 10.5 | 1.7 | 0.17001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
645 | 257e5ce9d8b142ae9310a56d23c8e60c | 1 MVA 20/0.4 kV DOTEL 1000/20 SGB |  | No action |  | 20.0 | 0.4 | 1.0 | 10.5 | 1.1 | 0.11001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
646 | b36bfb6021944791bca5456beca0e24e | 1 MVA 20/0.4 kV DTTH SGB |  | No action |  | 20.0 | 0.4 | 1.0 | 9.0 | 2.25 | 0.22501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
647 | b995813c72d24616a7539eb0f5871c48 | 1 MVA 20/0.4 kV DTTHIL SGB |  | No action |  | 20.0 | 0.4 | 1.0 | 6.5 | 1.73 | 0.17301 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
648 | b399063e39164b889f39293d16f2ba2e | 1 MVA 20/0.4 kV DTTHL SGB |  | No action |  | 20.0 | 0.4 | 1.0 | 8.7 | 1.55 | 0.15501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
649 | 2716f5ce778f438e9ad5a94cfb5d9e89 | 1 MVA 20/0.4 kV Dyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 1.0 | 9.6 | 1.75 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
650 | e4fd20f999394e20854fea8c8a745a57 | 1 MVA 20/0.4 kV Dyn1 ASEA |  | No action |  | 20.0 | 0.4 | 1.0 | 9.6 | 2.3 | 0.23001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
651 | cedd505661984b8fb9cc56268822bc2e | 1 MVA 20/0.4 kV Dyn1 wnr ASEA |  | No action |  | 20.0 | 0.4 | 1.0 | 9.6 | 1.75 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
652 | a51fcb142ffc4442b12843d4cd8e82c8 | 1 MVA 20/0.4 kV Dyn11 ASEA |  | No action |  | 20.0 | 0.4 | 1.0 | 9.6 | 2.3 | 0.23001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
653 | fbe209d00d254713a180d9fef56201b6 | 1 MVA 20/0.4 kV Dyn11 wnr ASEA |  | No action |  | 20.0 | 0.4 | 1.0 | 9.6 | 1.75 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
654 | 8b1f2bc633ba4cc996b8a29bb95fb017 | 1 MVA 20/0.4 kV Dyn5 ASEA |  | No action |  | 20.0 | 0.4 | 1.0 | 9.6 | 2.3 | 0.23001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
655 | 858c6f7f58ba475f873350019ea7d119 | 1 MVA 20/0.4 kV Dyn7 ASEA |  | No action |  | 20.0 | 0.4 | 1.0 | 9.6 | 2.3 | 0.23001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
656 | 4231d13a757e4c54b6ed58ecc308c941 | 1 MVA 20/0.4 kV Dyn7 wnr ASEA |  | No action |  | 20.0 | 0.4 | 1.0 | 9.6 | 1.75 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
657 | 5e3ea708e9c84916a4bd3dc2bcdf4242 | 1 MVA 20/0.4 kV Trafo Union |  | No action |  | 20.0 | 0.4 | 1.0 | 9.2 | 2.0 | 0.2 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
658 | aeb9ce88a0e04433baa7952c995fda41 | 1 MVA 20/0.4 kV Trafo Union wnr |  | No action |  | 20.0 | 0.4 | 1.0 | 9.0 | 1.8 | 0.18 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
659 | d9d9193c5d104123888ea9bd0817af37 | 1 MVA 20/0.4 kV Yyn0 ASEA |  | No action |  | 20.0 | 0.4 | 1.0 | 9.6 | 2.3 | 0.23001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
660 | 324a6f90b68a4153b4937c3ffce63850 | 1 MVA 20/0.4 kV Yyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 1.0 | 9.6 | 1.75 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
661 | 5542df9f457d4e01a8c232d5785a17f8 | 1 MVA 20/0.4 kV Yyn6 ASEA |  | No action |  | 20.0 | 0.4 | 1.0 | 9.6 | 2.3 | 0.23001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
662 | 7b80d30f6ac74637a604d2c38daf4fa2 | 1 MVA 20/0.4 kV Yyn6 wnr ASEA |  | No action |  | 20.0 | 0.4 | 1.0 | 9.6 | 1.75 | 0.17501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
663 | 27675545d4744aaf8b7cba04d04e0353 | 1.25 MVA 20/0.4 kV 2.11 GEAFOL |  | No action |  | 20.0 | 0.4 | 1.25 | 11.2 | 2.11 | 0.1688 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
664 | d9e598b867854c3d98cd00519ea65b98 | 1.25 MVA 20/0.4 kV 2.7 GEAFOL |  | No action |  | 20.0 | 0.4 | 1.25 | 10.4 | 2.7 | 0.216 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
665 | 4376fbb1c8ed4369a4a4563246949ac2 | 1.25 MVA 20/0.4 kV 2.7 GEAFOL/FC |  | No action |  | 20.0 | 0.4 | 1.25 | 10.4 | 2.7 | 0.216 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
666 | c4f1754a3de449ff8631372e078d7255 | 1.25 MVA 20/0.4 kV DOTE 1250/20 SGB |  | No action |  | 20.0 | 0.4 | 1.25 | 13.5 | 2.0 | 0.16001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
667 | b09fa8ad43ae46818f3cc8bd17bfe2bb | 1.25 MVA 20/0.4 kV DOTEL 1250/20 SGB |  | No action |  | 20.0 | 0.4 | 1.25 | 13.5 | 1.35 | 0.10801 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
668 | 5d02a66747ca4e8fa49dc854393e9b5d | 1.25 MVA 20/0.4 kV DTTH SGB |  | No action |  | 20.0 | 0.4 | 1.25 | 11.3 | 2.75 | 0.22001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
669 | fd939974e3a54f268391ac36d6ec6cdc | 1.25 MVA 20/0.4 kV DTTHIL SGB |  | No action |  | 20.0 | 0.4 | 1.25 | 7.6 | 2.2 | 0.17601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
670 | 0b9375f3b8ff45fb9545b3aaa4f88305 | 1.25 MVA 20/0.4 kV DTTHL SGB |  | No action |  | 20.0 | 0.4 | 1.25 | 10.6 | 2.0 | 0.16001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
671 | 09881624a2dd410394cead8373eca99d | 1.25 MVA 20/0.4 kV Dyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 1.25 | 11.5 | 2.08 | 0.16641 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
672 | f10433818dc14cce94c3acae28deaf5f | 1.25 MVA 20/0.4 kV Dyn1 ASEA |  | No action |  | 20.0 | 0.4 | 1.25 | 11.5 | 2.7 | 0.21601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
673 | e8494b551e5947b88de5cf770737c9ce | 1.25 MVA 20/0.4 kV Dyn1 wnr ASEA |  | No action |  | 20.0 | 0.4 | 1.25 | 11.5 | 2.08 | 0.16641 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
674 | 42e6a57b7e4348fbb31e9a81e253e6ba | 1.25 MVA 20/0.4 kV Dyn11 ASEA |  | No action |  | 20.0 | 0.4 | 1.25 | 11.5 | 2.7 | 0.21601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
675 | ab36ca4fc1b14f8b8114504824f3fbb2 | 1.25 MVA 20/0.4 kV Dyn11 wnr ASEA |  | No action |  | 20.0 | 0.4 | 1.25 | 11.5 | 2.08 | 0.16641 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
676 | 26f6ae0dec3349b0be702917691823d2 | 1.25 MVA 20/0.4 kV Dyn5 ASEA |  | No action |  | 20.0 | 0.4 | 1.25 | 11.5 | 2.7 | 0.21601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
677 | ce60dd73bf1549ac8ef576c9f26d8ab3 | 1.25 MVA 20/0.4 kV Dyn7 ASEA |  | No action |  | 20.0 | 0.4 | 1.25 | 11.5 | 2.7 | 0.21601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
678 | 15d87c7649904d17903b9a52e0a5046f | 1.25 MVA 20/0.4 kV Dyn7 wnr ASEA |  | No action |  | 20.0 | 0.4 | 1.25 | 11.5 | 2.08 | 0.16641 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
679 | cbe32fc05ee94047a40115994237558d | 1.25 MVA 20/0.4 kV Trafo Union |  | No action |  | 20.0 | 0.4 | 1.25 | 11.0 | 2.75 | 0.22 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
680 | 38385562802d47ab8ce87b1e05cea519 | 1.25 MVA 20/0.4 kV Trafo Union wnr |  | No action |  | 20.0 | 0.4 | 1.25 | 11.5 | 2.27 | 0.1816 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
681 | 734e0f2ad9c0446d87a6dac5d3a02321 | 1.25 MVA 20/0.4 kV Yyn0 ASEA |  | No action |  | 20.0 | 0.4 | 1.25 | 11.5 | 2.7 | 0.21601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
682 | 595790cfb6734c6099c20eec97d16f3b | 1.25 MVA 20/0.4 kV Yyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 1.25 | 11.5 | 2.08 | 0.16641 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
683 | 7b9fcb8d4f444ed3ab415e0705c102c7 | 1.25 MVA 20/0.4 kV Yyn6 ASEA |  | No action |  | 20.0 | 0.4 | 1.25 | 11.5 | 2.7 | 0.21601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
684 | 12230fe4ae8a4cf385fa7cee7de98c1b | 1.25 MVA 20/0.4 kV Yyn6 wnr ASEA |  | No action |  | 20.0 | 0.4 | 1.25 | 11.5 | 2.08 | 0.16641 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
685 | cfb95e494b8a429fa85bf85ef6a9b92b | 1.6 MVA 20/0.4 kV 2.42 GEAFOL |  | No action |  | 20.0 | 0.4 | 1.6 | 13.5 | 2.42 | 0.15125 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
686 | 656c48f942e54143a9f3834cdd9e70a1 | 1.6 MVA 20/0.4 kV 3.1 GEAFOL |  | No action |  | 20.0 | 0.4 | 1.6 | 11.7 | 3.1 | 0.19375 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
687 | 489d4a12a92a479387d390b8ce6f4389 | 1.6 MVA 20/0.4 kV DOTE 1600/20 SGB |  | No action |  | 20.0 | 0.4 | 1.6 | 17.0 | 2.2 | 0.13751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
688 | ca1a9c29c6574217b658769cefe4540c | 1.6 MVA 20/0.4 kV DOTEL 1600/20 SGB |  | No action |  | 20.0 | 0.4 | 1.6 | 17.0 | 1.6 | 0.10001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
689 | 00c82a362fa84794afb01a81ed43611c | 1.6 MVA 20/0.4 kV DTTH SGB |  | No action |  | 20.0 | 0.4 | 1.6 | 13.3 | 3.2 | 0.20001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
690 | eef8eb1c38114b6f85b7cb8750cba441 | 1.6 MVA 20/0.4 kV DTTHIL SGB |  | No action |  | 20.0 | 0.4 | 1.6 | 9.4 | 2.5 | 0.15626 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
691 | 909c455483824536b0caf1202e5d700a | 1.6 MVA 20/0.4 kV DTTHL SGB |  | No action |  | 20.0 | 0.4 | 1.6 | 13.0 | 2.25 | 0.140635 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
692 | e88e3801ca1d472aa5e5fc884ed8715d | 1.6 MVA 20/0.4 kV Dyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 1.6 | 14.0 | 2.4 | 0.15001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
693 | e8bd127f004e4b69ab1b6ec9fbc6793e | 1.6 MVA 20/0.4 kV Dyn1 ASEA |  | No action |  | 20.0 | 0.4 | 1.6 | 14.0 | 3.1 | 0.19376 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
694 | c71dbd92ef7a488cbc9b9f500d6e7918 | 1.6 MVA 20/0.4 kV Dyn1 wnr ASEA |  | No action |  | 20.0 | 0.4 | 1.6 | 14.0 | 2.4 | 0.15001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
695 | 65f08ce62dff4221b75d468f4236908f | 1.6 MVA 20/0.4 kV Dyn11 ASEA |  | No action |  | 20.0 | 0.4 | 1.6 | 14.0 | 3.1 | 0.19376 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
696 | 58d232d84a2c40c38deb8a2391da9080 | 1.6 MVA 20/0.4 kV Dyn11 wnr ASEA |  | No action |  | 20.0 | 0.4 | 1.6 | 14.0 | 2.4 | 0.15001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
697 | eba2fff663eb4250ae13e72787453859 | 1.6 MVA 20/0.4 kV Dyn5 ASEA |  | No action |  | 20.0 | 0.4 | 1.6 | 14.0 | 3.1 | 0.19376 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
698 | f36e7099c9624d34a1ca149c747fb477 | 1.6 MVA 20/0.4 kV Dyn7 ASEA |  | No action |  | 20.0 | 0.4 | 1.6 | 14.0 | 3.1 | 0.19376 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
699 | a6383c29eab14e378364d96b7b0aba66 | 1.6 MVA 20/0.4 kV Dyn7 wnr ASEA |  | No action |  | 20.0 | 0.4 | 1.6 | 14.0 | 2.4 | 0.15001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
700 | fd4253a4028944f88a22da2923698597 | 1.6 MVA 20/0.4 kV Trafo Union |  | No action |  | 20.0 | 0.4 | 1.6 | 12.3 | 3.1 | 0.19375 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
701 | c078b47c98ee46e998411a411c9e6598 | 1.6 MVA 20/0.4 kV Trafo Union wnr |  | No action |  | 20.0 | 0.4 | 1.6 | 12.8 | 2.55 | 0.159375 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
702 | 293c7c37504e490da4aabb1c977b55e6 | 1.6 MVA 20/0.4 kV Yyn0 ASEA |  | No action |  | 20.0 | 0.4 | 1.6 | 14.0 | 3.1 | 0.19376 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
703 | a4cc7b35e33144589639cebbe7e46ec3 | 1.6 MVA 20/0.4 kV Yyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 1.6 | 14.0 | 2.4 | 0.15001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
704 | 00cbecc8b7d64035816b0ee9ffdde6aa | 1.6 MVA 20/0.4 kV Yyn6 ASEA |  | No action |  | 20.0 | 0.4 | 1.6 | 14.0 | 3.1 | 0.19376 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
705 | 720dc8436e0f420994b4d20eb1f0c585 | 1.6 MVA 20/0.4 kV Yyn6 wnr ASEA |  | No action |  | 20.0 | 0.4 | 1.6 | 14.0 | 2.4 | 0.15001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
706 | c9725eb4ddc6464b83f654618743395d | 2 MVA 20/0.4 kV 3 GEAFOL |  | No action |  | 20.0 | 0.4 | 2.0 | 15.7 | 3.0 | 0.15 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
707 | 4c8097113a6949a7b498af81326df1c2 | 2 MVA 20/0.4 kV 4.5 GEAFOL |  | No action |  | 20.0 | 0.4 | 2.0 | 14.2 | 4.5 | 0.225 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
708 | f2cd7c1390ad4c428070982a497d6df7 | 2 MVA 20/0.4 kV DOTE 2000/20 SGB |  | No action |  | 20.0 | 0.4 | 2.0 | 21.5 | 2.9 | 0.14501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
709 | 50211d11ef594ac1967d74e4ee2c470d | 2 MVA 20/0.4 kV DOTEL 2000/20 SGB |  | No action |  | 20.0 | 0.4 | 2.0 | 21.5 | 2.1 | 0.10501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
710 | bed04823c1f84ffd8223d01c72b3605f | 2 MVA 20/0.4 kV DTTH SGB |  | No action |  | 20.0 | 0.4 | 2.0 | 16.9 | 4.3 | 0.21501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
711 | 783513ba5921492d86fa2a306caba44a | 2 MVA 20/0.4 kV DTTHIL SGB |  | No action |  | 20.0 | 0.4 | 2.0 | 12.5 | 3.1 | 0.15501 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
712 | 2bc48b10e1814827bf644247d455a18e | 2 MVA 20/0.4 kV DTTHL SGB |  | No action |  | 20.0 | 0.4 | 2.0 | 16.2 | 2.95 | 0.14751 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
713 | fd135a1943954cb5b17a9d8ac4d6eb5d | 2 MVA 20/0.4 kV Dyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 2.0 | 16.7 | 3.1 | 0.15501 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
714 | f60806849b6646839256bdc49cd8572c | 2 MVA 20/0.4 kV Dyn1 ASEA |  | No action |  | 20.0 | 0.4 | 2.0 | 16.7 | 4.0 | 0.20001 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
715 | 6f1e9ae4334c464fa282c25e91176f8a | 2 MVA 20/0.4 kV Dyn1 wnr ASEA |  | No action |  | 20.0 | 0.4 | 2.0 | 16.7 | 3.1 | 0.15501 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
716 | 2d4423791ce340ada29cad0b7d046f63 | 2 MVA 20/0.4 kV Dyn11 ASEA |  | No action |  | 20.0 | 0.4 | 2.0 | 16.7 | 4.0 | 0.20001 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
717 | 74ae08cfd256434fa6bb5a1bfd9d7059 | 2 MVA 20/0.4 kV Dyn11 wnr ASEA |  | No action |  | 20.0 | 0.4 | 2.0 | 16.7 | 3.1 | 0.15501 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
718 | 17c9a8f64e024211aee8d045208f5651 | 2 MVA 20/0.4 kV Dyn5 ASEA |  | No action |  | 20.0 | 0.4 | 2.0 | 16.7 | 4.0 | 0.20001 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
719 | 73e7144ed26f4f01a483ec0b626be820 | 2 MVA 20/0.4 kV Dyn7 ASEA |  | No action |  | 20.0 | 0.4 | 2.0 | 16.7 | 4.0 | 0.20001 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
720 | abac3f8cfd8d475aa48adf6c04a6ab97 | 2 MVA 20/0.4 kV Dyn7 wnr ASEA |  | No action |  | 20.0 | 0.4 | 2.0 | 16.7 | 3.1 | 0.15501 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
721 | d4e07b1891114d26a5338dcbb8950e3b | 2 MVA 20/0.4 kV Trafo Union |  | No action |  | 20.0 | 0.4 | 2.0 | 15.0 | 3.65 | 0.1825 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
722 | deb4dfbeaac5496380707289739d4c2e | 2 MVA 20/0.4 kV Trafo Union wnr |  | No action |  | 20.0 | 0.4 | 2.0 | 15.3 | 3.1 | 0.155 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
723 | 4532d81cc30a49f494ac3925028a3df7 | 2 MVA 20/0.4 kV Yyn0 ASEA |  | No action |  | 20.0 | 0.4 | 2.0 | 16.7 | 4.0 | 0.20001 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
724 | dfab92ebd60b444492634108c023d84a | 2 MVA 20/0.4 kV Yyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 2.0 | 16.7 | 3.1 | 0.15501 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
725 | e98859dadc354c5e96faa4e9438dd95e | 2 MVA 20/0.4 kV Yyn6 ASEA |  | No action |  | 20.0 | 0.4 | 2.0 | 16.7 | 4.0 | 0.20001 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
726 | 2a470a919678478ab4970833c5c2f3c3 | 2 MVA 20/0.4 kV Yyn6 wnr ASEA |  | No action |  | 20.0 | 0.4 | 2.0 | 16.7 | 3.1 | 0.15501 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
727 | 035288156939400ca3e2a06026b8304b | 2.5 MVA 20/0.4 kV 3.8 GEAFOL |  | No action |  | 20.0 | 0.4 | 2.5 | 19.3 | 3.8 | 0.152 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
728 | 7d0618fa9acc4f8a9d1c042a59d6c32f | 2.5 MVA 20/0.4 kV 5.3 GEAFOL |  | No action |  | 20.0 | 0.4 | 2.5 | 17.6 | 5.3 | 0.212 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
729 | 2edc54b249c14910a9e9a60769dda23d | 2.5 MVA 20/0.4 kV DOTE 2500/20 SGB |  | No action |  | 20.0 | 0.4 | 2.5 | 25.0 | 3.5 | 0.14001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
730 | b3072a61bed54437b814ac716d3994bf | 2.5 MVA 20/0.4 kV DOTEL 2500/20 SGB |  | No action |  | 20.0 | 0.4 | 2.5 | 25.0 | 2.5 | 0.10001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
731 | acd54fc940014aa5888a8d0e95fd977c | 2.5 MVA 20/0.4 kV DTTH SGB |  | No action |  | 20.0 | 0.4 | 2.5 | 19.0 | 4.7 | 0.18801 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
732 | d01c2f14ddab4f1d9b61e134738fb44c | 2.5 MVA 20/0.4 kV DTTHIL SGB |  | No action |  | 20.0 | 0.4 | 2.5 | 14.0 | 3.75 | 0.15001 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
733 | 212f31f140f444eebfed72fab634daf5 | 2.5 MVA 20/0.4 kV DTTHL SGB |  | No action |  | 20.0 | 0.4 | 2.5 | 18.5 | 3.4 | 0.13601 | 6.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
734 | 3ef644333f094472b1e599407444422b | 2.5 MVA 20/0.4 kV Dyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 2.5 | 20.0 | 3.8 | 0.15201 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
735 | dba7145ee14e4b76bef54b191fa15228 | 2.5 MVA 20/0.4 kV Dyn1 ASEA |  | No action |  | 20.0 | 0.4 | 2.5 | 20.0 | 5.0 | 0.20001 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
736 | e3bc3566c3c84e36812ec392441c2c31 | 2.5 MVA 20/0.4 kV Dyn1 wnr ASEA |  | No action |  | 20.0 | 0.4 | 2.5 | 20.0 | 3.8 | 0.15201 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
737 | 69a8abbcb7654dd1b0b91f5c9a997901 | 2.5 MVA 20/0.4 kV Dyn11 ASEA |  | No action |  | 20.0 | 0.4 | 2.5 | 20.0 | 5.0 | 0.20001 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
738 | 229c303297f6497597c6025f1b7526fe | 2.5 MVA 20/0.4 kV Dyn11 wnr ASEA |  | No action |  | 20.0 | 0.4 | 2.5 | 20.0 | 3.8 | 0.15201 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
739 | 2bad7541da934daca29ba3d8c32ec4ef | 2.5 MVA 20/0.4 kV Dyn5 ASEA |  | No action |  | 20.0 | 0.4 | 2.5 | 20.0 | 5.0 | 0.20001 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
740 | 1daf4e49552b48a3bc8d8522f7cdc8a8 | 2.5 MVA 20/0.4 kV Dyn7 ASEA |  | No action |  | 20.0 | 0.4 | 2.5 | 20.0 | 5.0 | 0.20001 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
741 | 4218f7b960184221b041dc2d256916b8 | 2.5 MVA 20/0.4 kV Dyn7 wnr ASEA |  | No action |  | 20.0 | 0.4 | 2.5 | 20.0 | 3.8 | 0.15201 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
742 | e4d6a4416868471392d4b5b19a66ba49 | 2.5 MVA 20/0.4 kV Trafo Union |  | No action |  | 20.0 | 0.4 | 2.5 | 17.5 | 3.95 | 0.158 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
743 | cb431e973b1f482191ed733bde72c26a | 2.5 MVA 20/0.4 kV Trafo Union wnr |  | No action |  | 20.0 | 0.4 | 2.5 | 18.0 | 3.35 | 0.134 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
744 | 596dc5a451a94524a54af073a91fa8b2 | 2.5 MVA 20/0.4 kV Yyn0 ASEA |  | No action |  | 20.0 | 0.4 | 2.5 | 20.0 | 5.0 | 0.20001 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
745 | a3bdb8c658704931ad67f798849f8030 | 2.5 MVA 20/0.4 kV Yyn0 wnr ASEA |  | No action |  | 20.0 | 0.4 | 2.5 | 20.0 | 3.8 | 0.15201 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
746 | 56d130f4738a4414805000d97ecb645f | 2.5 MVA 20/0.4 kV Yyn6 ASEA |  | No action |  | 20.0 | 0.4 | 2.5 | 20.0 | 5.0 | 0.20001 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
747 | 37d317cb5d1a4414b848f655cd771f9e | 2.5 MVA 20/0.4 kV Yyn6 wnr ASEA |  | No action |  | 20.0 | 0.4 | 2.5 | 20.0 | 3.8 | 0.15201 | 8.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
748 | 1a269867c8434fc5bec639a1cc903d2b | 210 MVA 132/15.75 kV |  | No action |  | 132.0 | 15.75 | 210.0 | 410.0 | 0.0 | 0.26 | 12.5 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
749 | 3d7acfabd8fe4503ae42ed84534df1cb | 25 MVA 20/10 kV |  | No action |  | 20.0 | 10.0 | 25.0 | 102.76 | 10.96 | 0.1 | 10.3 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
750 | 4b646de7882644c0ba8824c203132ffd | 255 MVA 380/19 kV |  | No action |  | 380.0 | 19.0 | 255.0 | 310.0 | 0.0 | 0.0 | 16.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
751 | 60f374f4a64b47318d0377acaf077ee5 | 47 MVA 33/11 kV |  | No action |  | 33.0 | 11.0 | 47.0 | 97.0 | 0.0 | 0.0 | 15.0 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
752 | 8232ad6ae1f4461e8cdf45c4c8efa251 | 50 MVA 139/10.5 kV |  | No action |  | 139.3 | 10.5 | 50.0 | 188.098 | 32.745 | 0.085 | 10.08 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
753 | 3ddc08309ce04e859bc862a82a020840 | 55 MVA 139/10.5 kV |  | No action |  | 139.3 | 10.5 | 55.0 | 168.743 | 31.51 | 0.078 | 10.04 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0
754 | 7a654817abbb459f83fb1bcf3a0f8164 | 90 MVA 132/33 kV |  | No action |  | 132.0 | 33.0 | 90.0 | 249.876 | 44.907 | 0.068 | 13.18 | NoRegulation | 5 | 0.01 | 2 | 90.0 | 1.0 | 1.0 | 0.0 | 0.0

## branch_group
idtag | name | code | action | comment | group_type

## transformer2w
idtag | name | code | action | comment | modelling_authority | bus_from | bus_to | cn_from | cn_to | active | reducible | rate | contingency_factor | protection_rating_factor | monitor_loading | mttf | mttr | Cost | build_status | capex | opex | group | ys | ysh | color | R | X | G | B | R0 | X0 | G0 | B0 | R2 | X2 | G2 | B2 | tolerance | tap_changer | tap_module | tap_module_max | tap_module_min | tap_module_control_mode | vset | Qset | regulation_bus | regulation_cn | tap_phase | tap_phase_max | tap_phase_min | tap_phase_control_mode | Pset | temp_base | temp_oper | alpha | HV | LV | Sn | Pcu | Pfe | I0 | Vsc | conn | template | possible_transformer_types

## windings
idtag | name | code | action | comment | modelling_authority | bus_from | bus_to | cn_from | cn_to | active | reducible | rate | contingency_factor | protection_rating_factor | monitor_loading | mttf | mttr | Cost | build_status | capex | opex | group | ys | ysh | color | R | X | G | B | R0 | X0 | G0 | B0 | R2 | X2 | G2 | B2 | tolerance | tap_changer | tap_module | tap_module_max | tap_module_min | tap_module_control_mode | vset | Qset | regulation_bus | regulation_cn | tap_phase | tap_phase_max | tap_phase_min | tap_phase_control_mode | Pset | temp_base | temp_oper | alpha | HV | LV | Sn | Pcu | Pfe | I0 | Vsc | conn | template | possible_transformer_types

## transformer3w
idtag | name | code | action | comment | modelling_authority | bus0 | bus1 | bus2 | bus3 | cn0 | cn1 | cn2 | cn3 | active | winding1 | winding2 | winding3 | V1 | V2 | V3 | r12 | r23 | r31 | x12 | x23 | x31 | rate1 | rate2 | rate3 | Pcu12 | Pcu23 | Pcu31 | Vsc12 | Vsc23 | Vsc31 | Pfe | I0 | x | y

## line
| idtag | name | code | action | comment | modelling_authority | bus_from | bus_to | cn_from | cn_to | active | reducible | rate | contingency_factor | protection_rating_factor | monitor_loading | mttf | mttr | Cost | build_status | capex | opex | group | ys | ysh | color | R | X | B | R0 | X0 | B0 | R2 | X2 | B2 | tolerance | circuit_idx | length | temp_base | temp_oper | alpha | r_fault | x_fault | fault_pos | template | locations | possible_tower_types | possible_underground_line_types | possible_sequence_line_types
0 | 545fe4426b29492eb207a919f331d3c2 | Line 1 |  | No action |  |  | 131557160c40462f9db94a50151714c3 | 1df58650151f42bb95a1fd1a375eee68 |  |  | True | False | 10.0 | 1.0 | 1.4 | True | 0.0 | 0.0 | 100.0 | Commissioned | 0.0 | 0.0 |  | <GridCalEngine.Devices.admittance_matrix.AdmittanceMatrix object at 0x0000028EC4D7E180> | <GridCalEngine.Devices.admittance_matrix.AdmittanceMatrix object at 0x0000028EC4D7EC90> | #909090 | 1e-08 | 0.001 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 0.0 | 0 | 1.0 | 20.0 | 20.0 | 0.0033 | 0.0 | 0.0 | 0.5 |  | 05424e0099e64cd8b7ff6fe76cc1db2d | {} | {} | {}
1 | ebb05b2f40e848b3be5f751177991ad2 | Line 2 |  | No action |  |  | 1df58650151f42bb95a1fd1a375eee68 | f9070e585ad14dc893b7b7680905459b |  |  | True | False | 10.0 | 1.0 | 1.4 | True | 0.0 | 0.0 | 100.0 | Commissioned | 0.0 | 0.0 |  | <GridCalEngine.Devices.admittance_matrix.AdmittanceMatrix object at 0x0000028EC4D7EFF0> | <GridCalEngine.Devices.admittance_matrix.AdmittanceMatrix object at 0x0000028EC4D7E2D0> | #909090 | 1e-08 | 0.01 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 0.0 | 0 | 1.0 | 20.0 | 20.0 | 0.0033 | 0.0 | 0.0 | 0.5 |  | 2b69b08109fd4c1e9b21cd856eacdd74 | {} | {} | {}
2 | ea46167001c4476a85bb1a7ddf0d4f23 | Line 3 |  | No action |  |  | f9070e585ad14dc893b7b7680905459b | 131557160c40462f9db94a50151714c3 |  |  | True | False | 10.0 | 1.0 | 1.4 | True | 0.0 | 0.0 | 100.0 | Commissioned | 0.0 | 0.0 |  | <GridCalEngine.Devices.admittance_matrix.AdmittanceMatrix object at 0x0000028EC4D7F3B0> | <GridCalEngine.Devices.admittance_matrix.AdmittanceMatrix object at 0x0000028EC4D7C110> | #909090 | 1e-08 | 0.001 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 0.0 | 0 | 1.0 | 20.0 | 20.0 | 0.0033 | 0.0 | 0.0 | 0.5 |  | 606c272a3a9145c0bdc35a51db24fb2b | {} | {} | {}
3 | 8473d3b1597e4682947e1c70b6a438f3 | Line 4 |  | No action |  |  | 1df58650151f42bb95a1fd1a375eee68 | 7563a5cdfc2843fbb2e2096a8f7a6a2d |  |  | True | False | 10.0 | 1.0 | 1.4 | True | 0.0 | 0.0 | 100.0 | Commissioned | 0.0 | 0.0 |  | <GridCalEngine.Devices.admittance_matrix.AdmittanceMatrix object at 0x0000028EC4D7FFE0> | <GridCalEngine.Devices.admittance_matrix.AdmittanceMatrix object at 0x0000028EC4D7FBC0> | #909090 | 1e-08 | 0.08 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 0.0 | 0 | 1.0 | 20.0 | 20.0 | 0.0033 | 0.0 | 0.0 | 0.5 |  | a1e8e681af2741238083f932f44521cc | {} | {} | {}
4 | 95b58245afe74469a907460f7717df8c | Line 5 |  | No action |  |  | 7563a5cdfc2843fbb2e2096a8f7a6a2d | 1cab1351b5d74c889a0212d3cdc0f341 |  |  | True | False | 10.0 | 1.0 | 1.4 | True | 0.0 | 0.0 | 100.0 | Commissioned | 0.0 | 0.0 |  | <GridCalEngine.Devices.admittance_matrix.AdmittanceMatrix object at 0x0000028EBF45C6B0> | <GridCalEngine.Devices.admittance_matrix.AdmittanceMatrix object at 0x0000028EBF45FFB0> | #909090 | 1e-08 | 0.08 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 0.0 | 0 | 1.0 | 20.0 | 20.0 | 0.0033 | 0.0 | 0.0 | 0.5 |  | a07a6051823b46bb8559b56a7870eeeb | {} | {} | {}
5 | 7710627659104c1d8e2e7da2a791e9c7 | Line 6 |  | No action |  |  | 1cab1351b5d74c889a0212d3cdc0f341 | 131557160c40462f9db94a50151714c3 |  |  | True | False | 10.0 | 1.0 | 1.4 | True | 0.0 | 0.0 | 100.0 | Commissioned | 0.0 | 0.0 |  | <GridCalEngine.Devices.admittance_matrix.AdmittanceMatrix object at 0x0000028EBF45DCA0> | <GridCalEngine.Devices.admittance_matrix.AdmittanceMatrix object at 0x0000028EBF45C830> | #909090 | 1e-08 | 0.001 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 1e-20 | 0.0 | 0 | 1.0 | 20.0 | 20.0 | 0.0033 | 0.0 | 0.0 | 0.5 |  | 8a408dd1b123499e81fea8cd7e9f4f7b | {} | {} | {}

## dc_line
idtag | name | code | action | comment | modelling_authority | bus_from | bus_to | cn_from | cn_to | active | reducible | rate | contingency_factor | protection_rating_factor | monitor_loading | mttf | mttr | Cost | build_status | capex | opex | group | ys | ysh | color | R | length | r_fault | fault_pos | template | locations

## hvdc
idtag | name | code | action | comment | modelling_authority | bus_from | bus_to | cn_from | cn_to | active | reducible | rate | contingency_factor | protection_rating_factor | monitor_loading | mttf | mttr | Cost | build_status | capex | opex | group | ys | ysh | color | dispatchable | control_mode | Pset | r | dc_link_voltage | angle_droop | Vset_f | Vset_t | min_firing_angle_f | max_firing_angle_f | min_firing_angle_t | max_firing_angle_t | length | locations

## vsc
idtag | name | code | action | comment | modelling_authority | bus_from | bus_to | cn_from | cn_to | active | reducible | rate | contingency_factor | protection_rating_factor | monitor_loading | mttf | mttr | Cost | build_status | capex | opex | group | ys | ysh | color | alpha1 | alpha2 | alpha3 | kdp | control1 | control2 | control1_val | control2_val | control1_dev | control2_dev

## upfc
idtag | name | code | action | comment | modelling_authority | bus_from | bus_to | cn_from | cn_to | active | reducible | rate | contingency_factor | protection_rating_factor | monitor_loading | mttf | mttr | Cost | build_status | capex | opex | group | ys | ysh | color | R | X | Rsh | Xsh | R0 | X0 | Rsh0 | Xsh0 | R2 | X2 | Rsh2 | Xsh2 | Vsh | Pfset | Qfset

## series_reactance
idtag | name | code | action | comment | modelling_authority | bus_from | bus_to | cn_from | cn_to | active | reducible | rate | contingency_factor | protection_rating_factor | monitor_loading | mttf | mttr | Cost | build_status | capex | opex | group | ys | ysh | color | R | X | R0 | X0 | R2 | X2 | tolerance | temp_base | temp_oper | alpha | r_fault | x_fault | fault_pos

## switch
idtag | name | code | action | comment | modelling_authority | bus_from | bus_to | cn_from | cn_to | active | reducible | rate | contingency_factor | protection_rating_factor | monitor_loading | mttf | mttr | Cost | build_status | capex | opex | group | ys | ysh | color | R | X | retained | normal_open | rated_current

## contingency_group
| idtag | name | code | action | comment | category
0 | 75c42d8e250445d0940d206dd4427dbb | Contingency 0 |  | No action |  | single

## contingency
| idtag | name | code | action | comment | device_idtag | prop | value | group
0 | ac53e9e784f145b38848de7abfc05f68 | Line 1 |  | No action |  | 545fe4426b29492eb207a919f331d3c2 | active | 0.0 | 75c42d8e250445d0940d206dd4427dbb

## remedial_action_group
idtag | name | code | action | comment | category | conn_group

## remedial_action
idtag | name | code | action | comment | device_idtag | prop | value | group

## investments_group
idtag | name | code | action | comment | category

## investment
idtag | name | code | action | comment | device_idtag | CAPEX | OPEX | status | group

## fluid_node
idtag | name | code | action | comment | modelling_authority | min_level | max_level | min_soc | max_soc | initial_level | bus | build_status | spillage_cost | inflow | color

## fluid_path
idtag | name | code | action | comment | modelling_authority | source | target | min_flow | max_flow | locations | color

## fluid_turbine
idtag | name | code | action | comment | modelling_authority | active | efficiency | max_flow_rate | plant | generator | build_status | facility

## fluid_pump
idtag | name | code | action | comment | modelling_authority | active | efficiency | max_flow_rate | plant | generator | build_status | facility

## fluid_p2x
idtag | name | code | action | comment | modelling_authority | active | efficiency | max_flow_rate | plant | generator | build_status | facility

## tower_wires
tower_name | wire_name | xpos | ypos | phase