## config
| Property | Value
0 | BaseMVA | 1000
1 | Version | 3
2 | Name | Nord pool model
3 | Comments | Converted from data from https://github.com/ALSETLab/Nordic44-Nordpool
4 | program | GridCal

## bus
| name | active | is_slack | Vnom | Vmin | Vmax | r_fault | x_fault | x | y | h | w | area | zone | substation
0 | 3000_FORSMARK | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -53188.0 | -87740.0 | 20.0 | 180.0 | Sweden | 23 | FORSMARK
1 | 3020_DANNEBO_HVDC | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -53473.0 | -87740.0 | 20.0 | 180.0 | Sweden | 23 | DANNEBO_HVDC
2 | 3100_HJALTA | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -53473.0 | -86884.0 | 20.0 | 180.0 | Sweden | 22 | HJALTA
3 | 3115_PORJUS | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -52902.0 | -86029.0 | 20.0 | 180.0 | Sweden | 21 | PORJUS
4 | 3200_TENHULT | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -54328.0 | -88596.0 | 20.0 | 180.0 | Sweden | 23 | TENHULT
5 | 3244_HOGASEN | True | False | 300.0 | 0.9 | 1.1 | 0 | 0 | -54328.0 | -88026.0 | 20.0 | 180.0 | Sweden | 22 | HOGASEN
6 | 3245_JARPSTROMMEN | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -54614.0 | -86884.0 | 20.0 | 180.0 | Sweden | 22 | JARPSTROMMEN
7 | 3249_GRUNDFORS | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -54049.0 | -86447.0 | 20.0 | 180.0 | Sweden | 22 | GRUNDFORS
8 | 3300_OSKARSHAMN | True | True | 420.0 | 0.9 | 1.1 | 0 | 0 | -53754.0 | -88617.0 | 20.0 | 180.0 | Sweden | 23 | OSKARSHAMN
9 | 3359_RINGHALS | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -54885.0 | -88504.0 | 20.0 | 180.0 | Sweden | 23 | RINGHALS
10 | 3360_STENKU_HVDC | True | False | 135.0 | 0.9 | 1.1 | 0 | 0 | -54044.0 | -87740.0 | 20.0 | 180.0 | Sweden | 23 | STENKU_HVDC
11 | 3701_AJAURE | True | False | 300.0 | 0.9 | 1.1 | 0 | 0 | -54035.0 | -86045.0 | 20.0 | 180.0 | Sweden | 22 | AJAURE
12 | 5100_TRETTEN | True | False | 300.0 | 0.9 | 1.1 | 0 | 0 | -55470.0 | -87455.0 | 20.0 | 180.0 | Norway | 11 | TRETTEN
13 | 5101_HASLE | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -55470.0 | -88026.0 | 20.0 | 180.0 | Norway | 11 | HASLE
14 | 5102_DAGALI | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -56002.0 | -87726.0 | 20.0 | 180.0 | Norway | 15 | DAGALI
15 | 5103_KONGSBERG | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -55766.0 | -88071.0 | 20.0 | 180.0 | Norway | 11 | KONGSBERG
16 | 5300_SIMA | True | False | 300.0 | 0.9 | 1.1 | 0 | 0 | -56586.0 | -87681.0 | 20.0 | 180.0 | Norway | 15 | SIMA
17 | 5301_AURLAND | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -56326.0 | -87740.0 | 20.0 | 180.0 | Norway | 15 | AURLAND
18 | 5304_GEILO | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -56037.0 | -87589.0 | 20.0 | 180.0 | Norway | 15 | GEILO
19 | 5305_EIDFJORD | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -56324.0 | -87592.0 | 20.0 | 180.0 | Norway | 15 | EIDFJORD
20 | 5400_OSLO1 | True | False | 300.0 | 0.9 | 1.1 | 0 | 0 | -55417.0 | -88009.0 | 20.0 | 180.0 | Norway | 11 | OSLO1
21 | 5401_SYLLING | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -55541.0 | -88118.0 | 20.0 | 180.0 | Norway | 11 | SYLLING
22 | 5402_KAGGEFOSS | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -55749.0 | -87894.0 | 20.0 | 180.0 | Norway | 11 | KAGGEFOSS
23 | 5500_OSLO2 | True | False | 300.0 | 0.9 | 1.1 | 0 | 0 | -55518.0 | -87819.0 | 20.0 | 180.0 | Norway | 11 | OSLO2
24 | 5501_SKIEN | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -55739.0 | -87751.0 | 20.0 | 180.0 | Norway | 11 | SKIEN
25 | 5600_KRISTIANSAND | True | False | 300.0 | 0.9 | 1.1 | 0 | 0 | -56040.0 | -88311.0 | 20.0 | 180.0 | Norway | 12 | KRISTIANSAND
26 | 5601_STAVANGER | True | False | 300.0 | 0.9 | 1.1 | 0 | 0 | -56896.0 | -88026.0 | 20.0 | 180.0 | Norway | 12 | STAVANGER
27 | 5602_SANDEFJORD | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -55467.0 | -88191.0 | 20.0 | 180.0 | Norway | 12 | SANDEFJORD
28 | 5603_ARENDAL | True | False | 300.0 | 0.9 | 1.1 | 0 | 0 | -55955.0 | -88364.0 | 20.0 | 180.0 | Norway | 12 | ARENDAL
29 | 5610_KRISTIA_HVDC | True | False | 300.0 | 0.9 | 1.1 | 0 | 0 | -56085.0 | -88465.0 | 20.0 | 180.0 | Norway | 12 | KRISTIA_HVDC
30 | 5620_FEDA_HVDC | True | False | 300.0 | 0.9 | 1.1 | 0 | 0 | -56611.0 | -88311.0 | 20.0 | 180.0 | Norway | 12 | FEDA_HVDC
31 | 6000_KVILLDAL | True | False | 300.0 | 0.9 | 1.1 | 0 | 0 | -56559.0 | -88085.0 | 20.0 | 180.0 | Norway | 12 | KVILLDAL
32 | 6001_HAGAFOSS | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -56039.0 | -87814.0 | 20.0 | 180.0 | Norway | 15 | HAGAFOSS
33 | 6100_BLAFALLI | True | False | 300.0 | 0.9 | 1.1 | 0 | 0 | -56719.0 | -87837.0 | 20.0 | 180.0 | Norway | 12 | BLAFALLI
34 | 6500_TRONDHEIM | True | False | 300.0 | 0.9 | 1.1 | 0 | 0 | -55470.0 | -86900.0 | 20.0 | 180.0 | Norway | 13 | TRONDHEIM
35 | 6700_ROSSAGA | True | False | 300.0 | 0.9 | 1.1 | 0 | 0 | -54614.0 | -86029.0 | 20.0 | 180.0 | Norway | 14 | ROSSAGA
36 | 6701_OFOTEN | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -53473.0 | -85458.0 | 20.0 | 180.0 | Norway | 14 | OFOTEN
37 | 7000_HELSINKI | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -51445.0 | -87886.0 | 20.0 | 180.0 | Finland | 31 | HELSINKI
38 | 7010_VYBORG_HVDC | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -50335.0 | -87455.0 | 20.0 | 180.0 | Finland | 31 | VYBORG_HVDC
39 | 7020_ESTLINK_HVDC | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -51500.0 | -87162.0 | 20.0 | 180.0 | Finland | 31 | ESTLINK_HVDC
40 | 7100_OULU | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -51191.0 | -86314.0 | 20.0 | 180.0 | Finland | 31 | OULU
41 | 8500_MALMO | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -54615.0 | -89210.0 | 20.0 | 180.0 | Sweden | 24 | MALMO
42 | 8600_ARRIE_HVDC | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -54614.0 | -88779.0 | 20.0 | 180.0 | Sweden | 24 | ARRIE_HVDC
43 | 8700_KARLSH_HVDC | True | False | 420.0 | 0.9 | 1.1 | 0 | 0 | -54328.0 | -88882.0 | 20.0 | 180.0 | Sweden | 24 | KARLSH_HVDC

## branch
| name | bus_from | bus_to | active | rate | mttf | mttr | R | X | G | B | tolerance | length | tap_module | angle | bus_to_regulated | vset | temp_base | temp_oper | alpha | r_fault | x_fault | fault_pos | branch_type | template
0 | Branch | 3000_FORSMARK | 3020_DANNEBO_HVDC | True | 2100.0 | 0.0 | 0.0 | 0.0 | 0.01 | 1.0000000000000001e-20 | 0.0 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
1 | Branch | 3000_FORSMARK | 3115_PORJUS | True | 3000.0 | 0.0 | 0.0 | 0.075 | 0.9 | 1.0000000000000001e-20 | 0.5 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
2 | Branch | 3000_FORSMARK | 3245_JARPSTROMMEN | True | 1800.0 | 0.0 | 0.0 | 0.008 | 0.12 | 1.0000000000000001e-20 | 0.05 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
3 | Branch | 3000_FORSMARK | 3245_JARPSTROMMEN | True | 1600.0 | 0.0 | 0.0 | 0.018000000000000002 | 0.2 | 1.0000000000000001e-20 | 0.05 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
4 | Branch | 3000_FORSMARK | 3300_OSKARSHAMN | True | 1400.0 | 0.0 | 0.0 | 0.006 | 0.08 | 1.0000000000000001e-20 | 0.03 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
5 | Branch | 3000_FORSMARK | 3300_OSKARSHAMN | True | 1400.0 | 0.0 | 0.0 | 0.009000000000000001 | 0.1 | 1.0000000000000001e-20 | 0.025 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
6 | Branch | 3100_HJALTA | 3115_PORJUS | True | 3000.0 | 0.0 | 0.0 | 0.015 | 0.2 | 1.0000000000000001e-20 | 0.2 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
7 | Branch | 3100_HJALTA | 3200_TENHULT | True | 2500.0 | 0.0 | 0.0 | 0.04 | 0.24 | 1.0000000000000001e-20 | 0.2 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
8 | Branch | 3100_HJALTA | 3200_TENHULT | True | 2500.0 | 0.0 | 0.0 | 0.04 | 0.24 | 1.0000000000000001e-20 | 0.2 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
9 | Branch | 3100_HJALTA | 3200_TENHULT | True | 2500.0 | 0.0 | 0.0 | 0.04 | 0.24 | 1.0000000000000001e-20 | 0.2 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
10 | Branch | 3100_HJALTA | 3249_GRUNDFORS | True | 3000.0 | 0.0 | 0.0 | 0.015 | 0.215 | 1.0000000000000001e-20 | 0.2 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
11 | Branch | 3100_HJALTA | 3359_RINGHALS | True | 1600.0 | 0.0 | 0.0 | 0.08 | 0.5 | 1.0000000000000001e-20 | 0.25 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
12 | Branch | 3100_HJALTA | 3359_RINGHALS | True | 2500.0 | 0.0 | 0.0 | 0.04 | 0.23 | 1.0000000000000001e-20 | 0.24 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
13 | Branch | 3115_PORJUS | 3245_JARPSTROMMEN | True | 2000.0 | 0.0 | 0.0 | 0.045 | 0.5 | 1.0000000000000001e-20 | 0.14 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
14 | Branch | 3115_PORJUS | 3249_GRUNDFORS | True | 1400.0 | 0.0 | 0.0 | 0.015 | 0.2 | 1.0000000000000001e-20 | 0.08 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
15 | Branch | 3115_PORJUS | 6701_OFOTEN | True | 1100.0 | 0.0 | 0.0 | 0.04 | 0.4 | 1.0000000000000001e-20 | 0.1 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
16 | Branch | 3115_PORJUS | 7100_OULU | True | 1700.0 | 0.0 | 0.0 | 0.04 | 0.13 | 1.0000000000000001e-20 | 0.13 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
17 | Branch | 3200_TENHULT | 3300_OSKARSHAMN | True | 1300.0 | 0.0 | 0.0 | 0.02 | 0.2 | 1.0000000000000001e-20 | 0.06 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
18 | Branch | 3200_TENHULT | 3359_RINGHALS | True | 2000.0 | 0.0 | 0.0 | 0.01 | 0.2 | 1.0000000000000001e-20 | 0.07 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
19 | Branch | 3200_TENHULT | 8500_MALMO | True | 2600.0 | 0.0 | 0.0 | 0.01 | 0.17 | 1.0000000000000001e-20 | 0.06 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
20 | Branch | 3244_HOGASEN | 6500_TRONDHEIM | True | 2500.0 | 0.0 | 0.0 | 0.01 | 0.2 | 1.0000000000000001e-20 | 0.06 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
21 | Branch | 3249_GRUNDFORS | 7100_OULU | True | 2600.0 | 0.0 | 0.0 | 0.02 | 0.075 | 1.0000000000000001e-20 | 0.078 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
22 | Branch | 3300_OSKARSHAMN | 8500_MALMO | True | 2600.0 | 0.0 | 0.0 | 0.02 | 0.23 | 1.0000000000000001e-20 | 0.06 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
23 | Branch | 3300_OSKARSHAMN | 8500_MALMO | True | 2600.0 | 0.0 | 0.0 | 0.012 | 0.27 | 1.0000000000000001e-20 | 0.1 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
24 | Branch | 3359_RINGHALS | 5101_HASLE | True | 2600.0 | 0.0 | 0.0 | 0.016 | 0.26 | 1.0000000000000001e-20 | 0.09 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
25 | Branch | 3359_RINGHALS | 5101_HASLE | True | 2500.0 | 0.0 | 0.0 | 0.02 | 0.22 | 1.0000000000000001e-20 | 0.06 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
26 | Branch | 3359_RINGHALS | 8500_MALMO | True | 2500.0 | 0.0 | 0.0 | 0.012 | 0.27 | 1.0000000000000001e-20 | 0.1 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
27 | Branch | 3359_RINGHALS | 8500_MALMO | True | 1400.0 | 0.0 | 0.0 | 0.025 | 0.32 | 1.0000000000000001e-20 | 0.09 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
28 | Branch | 3701_AJAURE | 6700_ROSSAGA | True | 500.0 | 0.0 | 0.0 | 0.25 | 2.0 | 1.0000000000000001e-20 | 0.03 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
29 | Branch | 5100_TRETTEN | 5500_OSLO2 | True | 900.0 | 0.0 | 0.0 | 0.027000000000000003 | 0.26 | 1.0000000000000001e-20 | 0.044000000000000004 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
30 | Branch | 5100_TRETTEN | 6500_TRONDHEIM | True | 950.0 | 0.0 | 0.0 | 0.08 | 0.9 | 1.0000000000000001e-20 | 0.06 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
31 | Branch | 5101_HASLE | 5102_DAGALI | True | 1900.0 | 0.0 | 0.0 | 0.008 | 0.1 | 1.0000000000000001e-20 | 0.09 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
32 | Branch | 5101_HASLE | 5103_KONGSBERG | True | 1800.0 | 0.0 | 0.0 | 0.01 | 0.14 | 1.0000000000000001e-20 | 0.04 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
33 | Branch | 5101_HASLE | 5501_SKIEN | True | 2500.0 | 0.0 | 0.0 | 0.01 | 0.15 | 1.0000000000000001e-20 | 0.55 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
34 | Branch | 5102_DAGALI | 5103_KONGSBERG | True | 2400.0 | 0.0 | 0.0 | 0.004 | 0.07 | 1.0000000000000001e-20 | 0.03 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
35 | Branch | 5102_DAGALI | 5304_GEILO | True | 2000.0 | 0.0 | 0.0 | 0.017 | 0.24 | 1.0000000000000001e-20 | 0.07 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
36 | Branch | 5102_DAGALI | 6001_HAGAFOSS | True | 2000.0 | 0.0 | 0.0 | 0.03 | 0.46 | 1.0000000000000001e-20 | 0.13 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
37 | Branch | 5103_KONGSBERG | 5304_GEILO | True | 2000.0 | 0.0 | 0.0 | 0.02 | 0.25 | 1.0000000000000001e-20 | 0.07 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
38 | Branch | 5103_KONGSBERG | 5304_GEILO | True | 2000.0 | 0.0 | 0.0 | 0.013000000000000001 | 0.2 | 1.0000000000000001e-20 | 0.06 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
39 | Branch | 5300_SIMA | 6100_BLAFALLI | True | 2600.0 | 0.0 | 0.0 | 0.021 | 0.22 | 1.0000000000000001e-20 | 0.01 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
40 | Branch | 5301_AURLAND | 5304_GEILO | True | 1700.0 | 0.0 | 0.0 | 0.01 | 0.2 | 1.0000000000000001e-20 | 0.06 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
41 | Branch | 5301_AURLAND | 5305_EIDFJORD | True | 2500.0 | 0.0 | 0.0 | 0.006999999999999999 | 0.12 | 1.0000000000000001e-20 | 0.031 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
42 | Branch | 5301_AURLAND | 6001_HAGAFOSS | True | 2150.0 | 0.0 | 0.0 | 0.013000000000000001 | 0.2 | 1.0000000000000001e-20 | 0.05 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
43 | Branch | 5304_GEILO | 5305_EIDFJORD | True | 2400.0 | 0.0 | 0.0 | 0.01 | 0.15 | 1.0000000000000001e-20 | 0.05 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
44 | Branch | 5304_GEILO | 5305_EIDFJORD | True | 1500.0 | 0.0 | 0.0 | 0.013000000000000001 | 0.017 | 1.0000000000000001e-20 | 0.04 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
45 | Branch | 5400_OSLO1 | 5500_OSLO2 | True | 2600.0 | 0.0 | 0.0 | 0.009000000000000001 | 0.094 | 1.0000000000000001e-20 | 0.05 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
46 | Branch | 5400_OSLO1 | 6000_KVILLDAL | True | 950.0 | 0.0 | 0.0 | 0.033 | 0.36 | 1.0000000000000001e-20 | 0.025 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
47 | Branch | 5401_SYLLING | 5501_SKIEN | True | 2000.0 | 0.0 | 0.0 | 0.0175 | 0.27 | 1.0000000000000001e-20 | 0.08 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
48 | Branch | 5401_SYLLING | 5602_SANDEFJORD | True | 2600.0 | 0.0 | 0.0 | 0.016 | 0.255 | 1.0000000000000001e-20 | 0.09 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
49 | Branch | 5401_SYLLING | 6001_HAGAFOSS | True | 1700.0 | 0.0 | 0.0 | 0.0064 | 0.1 | 1.0000000000000001e-20 | 0.027999999999999997 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
50 | Branch | 5402_KAGGEFOSS | 6001_HAGAFOSS | True | 3000.0 | 0.0 | 0.0 | 0.0007 | 0.01 | 1.0000000000000001e-20 | 0.003 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
51 | Branch | 5500_OSLO2 | 5603_ARENDAL | True | 950.0 | 0.0 | 0.0 | 0.05 | 0.6 | 1.0000000000000001e-20 | 0.05 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
52 | Branch | 5600_KRISTIANSAND | 5601_STAVANGER | True | 1800.0 | 0.0 | 0.0 | 0.03 | 0.34 | 1.0000000000000001e-20 | 0.02 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
53 | Branch | 5600_KRISTIANSAND | 5603_ARENDAL | True | 3500.0 | 0.0 | 0.0 | 0.02 | 0.22 | 1.0000000000000001e-20 | 0.02 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
54 | Branch | 5600_KRISTIANSAND | 5620_FEDA_HVDC | True | 1500.0 | 0.0 | 0.0 | 0.0 | 0.01 | 1.0000000000000001e-20 | 0.0 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
55 | Branch | 5600_KRISTIANSAND | 6000_KVILLDAL | True | 2900.0 | 0.0 | 0.0 | 0.02 | 0.2 | 1.0000000000000001e-20 | 0.07 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
56 | Branch | 5603_ARENDAL | 5610_KRISTIA_HVDC | True | 3500.0 | 0.0 | 0.0 | 0.0 | 0.01 | 1.0000000000000001e-20 | 0.0 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
57 | Branch | 6000_KVILLDAL | 6100_BLAFALLI | True | 2400.0 | 0.0 | 0.0 | 0.034 | 0.42 | 1.0000000000000001e-20 | 0.03 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
58 | Branch | 6500_TRONDHEIM | 6700_ROSSAGA | True | 950.0 | 0.0 | 0.0 | 0.17 | 1.8 | 1.0000000000000001e-20 | 0.1 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
59 | Branch | 6500_TRONDHEIM | 6700_ROSSAGA | True | 1300.0 | 0.0 | 0.0 | 0.1 | 1.3 | 1.0000000000000001e-20 | 0.12 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
60 | Branch | 7000_HELSINKI | 7010_VYBORG_HVDC | True | 3500.0 | 0.0 | 0.0 | 0.0 | 0.01 | 1.0000000000000001e-20 | 0.0 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
61 | Branch | 7000_HELSINKI | 7020_ESTLINK_HVDC | True | 1500.0 | 0.0 | 0.0 | 0.0 | 0.01 | 1.0000000000000001e-20 | 0.0 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
62 | Branch | 7000_HELSINKI | 7100_OULU | True | 1500.0 | 0.0 | 0.0 | 0.04 | 0.12 | 1.0000000000000001e-20 | 0.13 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
63 | Branch | 7000_HELSINKI | 7100_OULU | True | 1500.0 | 0.0 | 0.0 | 0.04 | 0.12 | 1.0000000000000001e-20 | 0.13 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
64 | Branch | 7000_HELSINKI | 7100_OULU | True | 1700.0 | 0.0 | 0.0 | 0.04 | 0.14 | 1.0000000000000001e-20 | 0.13 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
65 | Branch | 8500_MALMO | 8600_ARRIE_HVDC | True | 1500.0 | 0.0 | 0.0 | 0.0 | 0.01 | 1.0000000000000001e-20 | 0.0 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
66 | Branch | 8500_MALMO | 8700_KARLSH_HVDC | True | 1500.0 | 0.0 | 0.0 | 0.0 | 0.01 | 1.0000000000000001e-20 | 0.0 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | line | BranchTemplate
67 | 1 | 3244_HOGASEN | 3245_JARPSTROMMEN | True | 4000.0 | 0.0 | 0.0 | 0.005 | 0.02 | 0.0 | 0.0 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | transformer | BranchTemplate
68 | 1 | 3701_AJAURE | 3249_GRUNDFORS | True | 4000.0 | 0.0 | 0.0 | 0.02 | 0.5 | 0.0 | 0.0 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | transformer | BranchTemplate
69 | 1 | 3359_RINGHALS | 3360_STENKU_HVDC | True | 4000.0 | 0.0 | 0.0 | 0.005 | 0.02 | 0.0 | 0.0 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | transformer | BranchTemplate
70 | 1 | 5101_HASLE | 5100_TRETTEN | True | 4000.0 | 0.0 | 0.0 | 0.0008 | 0.0305 | 0.0 | 0.0 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | transformer | BranchTemplate
71 | 1 | 5300_SIMA | 5301_AURLAND | True | 5000.0 | 0.0 | 0.0 | 0.0016 | 0.061 | 0.0 | 0.0 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | transformer | BranchTemplate
72 | 1 | 5400_OSLO1 | 5401_SYLLING | True | 4000.0 | 0.0 | 0.0 | 0.0032 | 0.12 | 0.0 | 0.0 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | transformer | BranchTemplate
73 | 1 | 5400_OSLO1 | 5402_KAGGEFOSS | True | 4000.0 | 0.0 | 0.0 | 0.0004 | 0.015 | 0.0 | 0.0 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | transformer | BranchTemplate
74 | 1 | 5500_OSLO2 | 5501_SKIEN | True | 4000.0 | 0.0 | 0.0 | 0.0004 | 0.015 | 0.0 | 0.0 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | transformer | BranchTemplate
75 | 1 | 5601_STAVANGER | 6001_HAGAFOSS | True | 4000.0 | 0.0 | 0.0 | 0.0002 | 0.0076 | 0.0 | 0.0 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | transformer | BranchTemplate
76 | 1 | 5603_ARENDAL | 5602_SANDEFJORD | True | 4000.0 | 0.0 | 0.0 | 0.0008 | 0.0305 | 0.0 | 0.0 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | transformer | BranchTemplate
77 | 1 | 6000_KVILLDAL | 6001_HAGAFOSS | True | 4000.0 | 0.0 | 0.0 | 0.0004 | 0.015 | 0.0 | 0.0 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | transformer | BranchTemplate
78 | 1 | 6700_ROSSAGA | 6701_OFOTEN | True | 4000.0 | 0.0 | 0.0 | 0.005 | 0.02 | 0.0 | 0.0 | 0 | 1.0 | 1.0 | 0.0 | False | 1.0 | 20 | 20 | 0.0033 | 0.0 | 0.0 | 0.5 | transformer | BranchTemplate

## load
| name | bus | active | P | Q | Ir | Ii | G | B | mttf | mttr
0 | Load '1 ' | 3000_FORSMARK | TRUE | 293.761 | 99.393 | 0 | 0 | 0 | 0 | 0 | 0
1 | Load '2 ' | 3000_FORSMARK | TRUE | 293.761 | 99.393 | 0 | 0 | 0 | 0 | 0 | 0
2 | Load '3 ' | 3000_FORSMARK | TRUE | 293.761 | 99.393 | 0 | 0 | 0 | 0 | 0 | 0
3 | Load '1 ' | 3020_DANNEBO_HVDC | TRUE | 1220 | 400.995 | 0 | 0 | 0 | 0 | 0 | 0
4 | Load '1 ' | 3100_HJALTA | TRUE | 90.183 | 94.384 | 0 | 0 | 0 | 0 | 0 | 0
5 | Load '1 ' | 3115_PORJUS | TRUE | 1029 | 338.216 | 0 | 0 | 0 | 0 | 0 | 0
6 | Load '1 ' | 3249_GRUNDFORS | TRUE | 1893.817 | 557.725 | 0 | 0 | 0 | 0 | 0 | 0
7 | Load '1 ' | 3300_OSKARSHAMN | TRUE | 1285.4 | 358.053 | 0 | 0 | 0 | 0 | 0 | 0
8 | Load '2 ' | 3300_OSKARSHAMN | TRUE | 1285.4 | 358.053 | 0 | 0 | 0 | 0 | 0 | 0
9 | Load '1 ' | 3359_RINGHALS | TRUE | 1542.479 | 537.078 | 0 | 0 | 0 | 0 | 0 | 0
10 | Load '2 ' | 3359_RINGHALS | TRUE | 1542.479 | 537.078 | 0 | 0 | 0 | 0 | 0 | 0
11 | Load '3 ' | 3359_RINGHALS | TRUE | 1542.479 | 537.078 | 0 | 0 | 0 | 0 | 0 | 0
12 | Load '4 ' | 3359_RINGHALS | TRUE | 1542.479 | 537.078 | 0 | 0 | 0 | 0 | 0 | 0
13 | Load '1 ' | 3360_STENKU_HVDC | TRUE | -80 | -26.295 | 0 | 0 | 0 | 0 | 0 | 0
14 | Load '1 ' | 5100_TRETTEN | TRUE | 586.618 | 163.598 | 0 | 0 | 0 | 0 | 0 | 0
15 | Load '2 ' | 5300_SIMA | TRUE | 2303 | 756.959 | 0 | 0 | 0 | 0 | 0 | 0
16 | Load '1 ' | 5400_OSLO1 | TRUE | 1226.567 | 233.71 | 0 | 0 | 0 | 0 | 0 | 0
17 | Load '1 ' | 5500_OSLO2 | TRUE | 1119.908 | 467.424 | 0 | 0 | 0 | 0 | 0 | 0
18 | Load '2 ' | 5500_OSLO2 | TRUE | 1119.908 | 467.424 | 0 | 0 | 0 | 0 | 0 | 0
19 | Load '1 ' | 5600_KRISTIANSAND | TRUE | 1397.946 | 284.835 | 0 | 0 | 0 | 0 | 0 | 0
20 | Load '2 ' | 5600_KRISTIANSAND | TRUE | 1397.946 | 284.835 | 0 | 0 | 0 | 0 | 0 | 0
21 | Load '1 ' | 5610_KRISTIA_HVDC | TRUE | -1584 | -225.708 | 0 | 0 | 0 | 0 | 0 | 0
22 | Load '1 ' | 5620_FEDA_HVDC | TRUE | 727 | 238.953 | 0 | 0 | 0 | 0 | 0 | 0
23 | Load '1 ' | 6100_BLAFALLI | TRUE | 714.054 | 261.882 | 0 | 0 | 0 | 0 | 0 | 0
24 | Load '2 ' | 6100_BLAFALLI | TRUE | 714.054 | 261.882 | 0 | 0 | 0 | 0 | 0 | 0
25 | Load '1 ' | 6500_TRONDHEIM | TRUE | 832.667 | 273.684 | 0 | 0 | 0 | 0 | 0 | 0
26 | Load '2 ' | 6500_TRONDHEIM | TRUE | 832.667 | 273.684 | 0 | 0 | 0 | 0 | 0 | 0
27 | Load '3 ' | 6500_TRONDHEIM | TRUE | 832.667 | 273.684 | 0 | 0 | 0 | 0 | 0 | 0
28 | Load '1 ' | 6700_ROSSAGA | TRUE | 2256 | 741.511 | 0 | 0 | 0 | 0 | 0 | 0
29 | Load '1 ' | 6701_OFOTEN | TRUE | -36 | -11.833 | 0 | 0 | 0 | 0 | 0 | 0
30 | Load '3 ' | 6701_OFOTEN | TRUE | -18 | -5.916 | 0 | 0 | 0 | 0 | 0 | 0
31 | Load '1 ' | 7000_HELSINKI | TRUE | 1372.248 | 286.124 | 0 | 0 | 0 | 0 | 0 | 0
32 | Load '2 ' | 7000_HELSINKI | TRUE | 1372.248 | 286.124 | 0 | 0 | 0 | 0 | 0 | 0
33 | Load '3 ' | 7000_HELSINKI | TRUE | 1372.248 | 286.124 | 0 | 0 | 0 | 0 | 0 | 0
34 | Load '4 ' | 7000_HELSINKI | TRUE | 1372.248 | 286.124 | 0 | 0 | 0 | 0 | 0 | 0
35 | Load '5 ' | 7000_HELSINKI | TRUE | 1372.248 | 286.124 | 0 | 0 | 0 | 0 | 0 | 0
36 | Load '6 ' | 7000_HELSINKI | TRUE | -1220 | -400.995 | 0 | 0 | 0 | 0 | 0 | 0
37 | Load '1 ' | 7010_VYBORG_HVDC | TRUE | -1005 | -330.328 | 0 | 0 | 0 | 0 | 0 | 0
38 | Load '1 ' | 7020_ESTLINK_HVDC | TRUE | 719 | 236.324 | 0 | 0 | 0 | 0 | 0 | 0
39 | Load '1 ' | 7100_OULU | TRUE | 1232.879 | 817.509 | 0 | 0 | 0 | 0 | 0 | 0
40 | Load '2 ' | 7100_OULU | TRUE | 1232.879 | 817.509 | 0 | 0 | 0 | 0 | 0 | 0
41 | Load '3 ' | 7100_OULU | TRUE | 36 | 11.833 | 0 | 0 | 0 | 0 | 0 | 0
42 | Load '1 ' | 8500_MALMO | TRUE | 963.667 | 316.742 | 0 | 0 | 0 | 0 | 0 | 0
43 | Load '2 ' | 8500_MALMO | TRUE | 963.667 | 316.742 | 0 | 0 | 0 | 0 | 0 | 0
44 | Load '3 ' | 8500_MALMO | TRUE | 963.667 | 316.742 | 0 | 0 | 0 | 0 | 0 | 0
45 | Load '4 ' | 8500_MALMO | TRUE | -400 | -131.474 | 0 | 0 | 0 | 0 | 0 | 0
46 | Load '1 ' | 8600_ARRIE_HVDC | TRUE | -76 | -24.98 | 0 | 0 | 0 | 0 | 0 | 0
47 | Load '1 ' | 8700_KARLSH_HVDC | TRUE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## static_generator
name | bus | active | P | Q | mttf | mttr

## battery
name | bus | active | is_controlled | P | Pf | Vset | Snom | Enom | max_soc | min_soc | soc_0 | charge_efficiency | discharge_efficiency | discharge_per_cycle | Qmin | Qmax | Pmin | Pmax | Cost | enabled_dispatch | mttf | mttr

## generator
| name | bus | active | is_controlled | P | Pf | Vset | Snom | Qmin | Qmax | Pmin | Pmax | Cost | enabled_dispatch | mttf | mttr
0 | Gen_'1 ' | 3000_FORSMARK | TRUE | TRUE | 371.233 | 0.8 | 1 | 1300 | -967 | 967 | 0 | 9999 | 1 | TRUE | 0 | 0
1 | Gen_'2 ' | 3000_FORSMARK | TRUE | TRUE | 371.233 | 0.8 | 1 | 1300 | -967 | 967 | 0 | 9999 | 1 | TRUE | 0 | 0
2 | Gen_'3 ' | 3000_FORSMARK | TRUE | TRUE | 371.233 | 0.8 | 1 | 1300 | -967 | 967 | 0 | 9999 | 1 | TRUE | 0 | 0
3 | Gen_'1 ' | 3115_PORJUS | TRUE | TRUE | 316.4 | 0.8 | 1 | 1100 | -933 | 933 | 0 | 9999 | 1 | TRUE | 0 | 0
4 | Gen_'2 ' | 3115_PORJUS | TRUE | TRUE | 316.4 | 0.8 | 1 | 1100 | -933 | 933 | 0 | 9999 | 1 | TRUE | 0 | 0
5 | Gen_'3 ' | 3115_PORJUS | TRUE | TRUE | 316.4 | 0.8 | 1 | 1100 | -933 | 933 | 0 | 9999 | 1 | TRUE | 0 | 0
6 | Gen_'4 ' | 3115_PORJUS | TRUE | TRUE | 316.4 | 0.8 | 1 | 1100 | -933 | 933 | 0 | 9999 | 1 | TRUE | 0 | 0
7 | Gen_'5 ' | 3115_PORJUS | TRUE | TRUE | 316.4 | 0.8 | 1 | 1100 | -933 | 933 | 0 | 9999 | 1 | TRUE | 0 | 0
8 | Gen_'1 ' | 3245_JARPSTROMMEN | TRUE | TRUE | 200.27 | 0.8 | 1 | 950 | -670 | 670 | 0 | 9999 | 1 | TRUE | 0 | 0
9 | Gen_'1 ' | 3249_GRUNDFORS | TRUE | TRUE | 439.841 | 0.8 | 1 | 1357 | -986 | 986 | 0 | 9999 | 1 | TRUE | 0 | 0
10 | Gen_'2 ' | 3249_GRUNDFORS | TRUE | TRUE | 439.841 | 0.8 | 1 | 1357 | -986 | 986 | 0 | 9999 | 1 | TRUE | 0 | 0
11 | Gen_'3 ' | 3249_GRUNDFORS | TRUE | TRUE | 439.841 | 0.8 | 1 | 1357 | -986 | 986 | 0 | 9999 | 1 | TRUE | 0 | 0
12 | Gen_'4 ' | 3249_GRUNDFORS | TRUE | TRUE | 439.841 | 0.8 | 1 | 1357 | -986 | 986 | 0 | 9999 | 1 | TRUE | 0 | 0
13 | Gen_'5 ' | 3249_GRUNDFORS | TRUE | TRUE | 439.841 | 0.8 | 1 | 1357 | -986 | 986 | 0 | 9999 | 1 | TRUE | 0 | 0
14 | Gen_'6 ' | 3249_GRUNDFORS | TRUE | TRUE | 439.841 | 0.8 | 1 | 1357 | -986 | 986 | 0 | 9999 | 1 | TRUE | 0 | 0
15 | Gen_'7 ' | 3249_GRUNDFORS | TRUE | TRUE | 439.841 | 0.8 | 1 | 1357 | -986 | 986 | 0 | 9999 | 1 | TRUE | 0 | 0
16 | Gen_'8 ' | 3249_GRUNDFORS | TRUE | TRUE | 439.841 | 0.8 | 1 | 1357 | -986 | 986 | 0 | 9999 | 1 | TRUE | 0 | 0
17 | Gen_'1 ' | 3300_OSKARSHAMN | TRUE | TRUE | 704.102 | 0.8 | 1 | 1100 | -767 | 767 | 0 | 9999 | 1 | TRUE | 0 | 0
18 | Gen_'2 ' | 3300_OSKARSHAMN | TRUE | TRUE | 704.102 | 0.8 | 1 | 1100 | -767 | 767 | 0 | 9999 | 1 | TRUE | 0 | 0
19 | Gen_'3 ' | 3300_OSKARSHAMN | TRUE | TRUE | 704.102 | 0.8 | 1 | 1100 | -767 | 767 | 0 | 9999 | 1 | TRUE | 0 | 0
20 | Gen_'4 ' | 3300_OSKARSHAMN | TRUE | TRUE | 704.102 | 0.8 | 1 | 1100 | -767 | 767 | 0 | 9999 | 1 | TRUE | 0 | 0
21 | Gen_'5 ' | 3300_OSKARSHAMN | TRUE | TRUE | 704.102 | 0.8 | 1 | 1100 | -767 | 767 | 0 | 9999 | 1 | TRUE | 0 | 0
22 | Gen_'6 ' | 3300_OSKARSHAMN | TRUE | TRUE | 704.102 | 0.8 | 1 | 1100 | -767 | 767 | 0 | 9999 | 1 | TRUE | 0 | 0
23 | Gen_'1 ' | 3359_RINGHALS | TRUE | TRUE | 698.949 | 0.8 | 1 | 1350 | -983 | 983 | 0 | 9999 | 1 | TRUE | 0 | 0
24 | Gen_'2 ' | 3359_RINGHALS | TRUE | TRUE | 698.949 | 0.8 | 1 | 1350 | -983 | 983 | 0 | 9999 | 1 | TRUE | 0 | 0
25 | Gen_'3 ' | 3359_RINGHALS | TRUE | TRUE | 698.949 | 0.8 | 1 | 1350 | -983 | 983 | 0 | 9999 | 1 | TRUE | 0 | 0
26 | Gen_'4 ' | 3359_RINGHALS | TRUE | TRUE | 698.949 | 0.8 | 1 | 1350 | -983 | 983 | 0 | 9999 | 1 | TRUE | 0 | 0
27 | Gen_'5 ' | 3359_RINGHALS | TRUE | TRUE | 698.949 | 0.8 | 1 | 1350 | -983 | 983 | 0 | 9999 | 1 | TRUE | 0 | 0
28 | Gen_'6 ' | 3359_RINGHALS | TRUE | TRUE | 698.949 | 0.8 | 1 | 1350 | -983 | 983 | 0 | 9999 | 1 | TRUE | 0 | 0
29 | Gen_'1 ' | 5100_TRETTEN | TRUE | TRUE | 351.755 | 0.8 | 1 | 1200 | -850 | 850 | 0 | 9999 | 1 | TRUE | 0 | 0
30 | Gen_'2 ' | 5100_TRETTEN | TRUE | TRUE | 351.755 | 0.8 | 1 | 1200 | -850 | 850 | 0 | 9999 | 1 | TRUE | 0 | 0
31 | Gen_'1 ' | 5300_SIMA | TRUE | TRUE | 723.333 | 0.8 | 1 | 1200 | -850 | 850 | 0 | 9999 | 1 | TRUE | 0 | 0
32 | Gen_'2 ' | 5300_SIMA | TRUE | TRUE | 723.333 | 0.8 | 1 | 1200 | -850 | 850 | 0 | 9999 | 1 | TRUE | 0 | 0
33 | Gen_'3 ' | 5300_SIMA | TRUE | TRUE | 723.333 | 0.8 | 1 | 1200 | -850 | 850 | 0 | 9999 | 1 | TRUE | 0 | 0
34 | Gen_'4 ' | 5300_SIMA | TRUE | TRUE | 723.333 | 0.8 | 1 | 1200 | -850 | 850 | 0 | 9999 | 1 | TRUE | 0 | 0
35 | Gen_'5 ' | 5300_SIMA | TRUE | TRUE | 723.333 | 0.8 | 1 | 1200 | -850 | 850 | 0 | 9999 | 1 | TRUE | 0 | 0
36 | Gen_'6 ' | 5300_SIMA | TRUE | TRUE | 723.333 | 0.8 | 1 | 1200 | -850 | 850 | 0 | 9999 | 1 | TRUE | 0 | 0
37 | Gen_'1 ' | 5400_OSLO1 | TRUE | TRUE | 333.242 | 0.8 | 1.007 | 1225 | -900 | 900 | 0 | 9999 | 1 | TRUE | 0 | 0
38 | Gen_'2 ' | 5400_OSLO1 | TRUE | TRUE | 333.242 | 0.8 | 1.007 | 1225 | -900 | 900 | 0 | 9999 | 1 | TRUE | 0 | 0
39 | Gen_'1 ' | 5500_OSLO2 | TRUE | TRUE | 259.503 | 0.8 | 1.004 | 1450 | -1200 | 1200 | 0 | 9999 | 1 | TRUE | 0 | 0
40 | Gen_'2 ' | 5500_OSLO2 | TRUE | TRUE | 259.503 | 0.8 | 1.004 | 1450 | -1200 | 1200 | 0 | 9999 | 1 | TRUE | 0 | 0
41 | Gen_'1 ' | 5600_KRISTIANSAND | TRUE | TRUE | 236.38 | 0.8 | 1.01 | 1650 | -850 | 850 | 0 | 9999 | 1 | TRUE | 0 | 0
42 | Gen_'2 ' | 5600_KRISTIANSAND | TRUE | TRUE | 236.38 | 0.8 | 1.01 | 1650 | -850 | 850 | 0 | 9999 | 1 | TRUE | 0 | 0
43 | Gen_'3 ' | 5600_KRISTIANSAND | TRUE | TRUE | 236.38 | 0.8 | 1.01 | 1650 | -850 | 850 | 0 | 9999 | 1 | TRUE | 0 | 0
44 | Gen_'4 ' | 5600_KRISTIANSAND | TRUE | TRUE | 236.38 | 0.8 | 1.01 | 1650 | -850 | 850 | 0 | 9999 | 1 | TRUE | 0 | 0
45 | Gen_'1 ' | 6000_KVILLDAL | TRUE | TRUE | 429.844 | 0.8 | 1.005 | 680 | -500 | 500 | 0 | 9999 | 1 | TRUE | 0 | 0
46 | Gen_'2 ' | 6000_KVILLDAL | TRUE | TRUE | 429.844 | 0.8 | 1.005 | 680 | -500 | 500 | 0 | 9999 | 1 | TRUE | 0 | 0
47 | Gen_'3 ' | 6000_KVILLDAL | TRUE | TRUE | 429.844 | 0.8 | 1.005 | 680 | -500 | 500 | 0 | 9999 | 1 | TRUE | 0 | 0
48 | Gen_'4 ' | 6000_KVILLDAL | TRUE | TRUE | 429.844 | 0.8 | 1.005 | 680 | -500 | 500 | 0 | 9999 | 1 | TRUE | 0 | 0
49 | Gen_'1 ' | 6100_BLAFALLI | TRUE | TRUE | 628.821 | 0.8 | 1 | 1240 | -900 | 900 | 0 | 9999 | 1 | TRUE | 0 | 0
50 | Gen_'2 ' | 6100_BLAFALLI | TRUE | TRUE | 628.821 | 0.8 | 1 | 1240 | -900 | 900 | 0 | 9999 | 1 | TRUE | 0 | 0
51 | Gen_'3 ' | 6100_BLAFALLI | TRUE | TRUE | 628.821 | 0.8 | 1 | 1240 | -900 | 900 | 0 | 9999 | 1 | TRUE | 0 | 0
52 | Gen_'4 ' | 6100_BLAFALLI | TRUE | TRUE | 628.821 | 0.8 | 1 | 1240 | -900 | 900 | 0 | 9999 | 1 | TRUE | 0 | 0
53 | Gen_'5 ' | 6100_BLAFALLI | TRUE | TRUE | 628.821 | 0.8 | 1 | 1240 | -900 | 900 | 0 | 9999 | 1 | TRUE | 0 | 0
54 | Gen_'1 ' | 6500_TRONDHEIM | TRUE | TRUE | 201.25 | 0.8 | 1 | 1100 | -800 | 800 | 0 | 9999 | 1 | TRUE | 0 | 0
55 | Gen_'2 ' | 6500_TRONDHEIM | TRUE | TRUE | 201.25 | 0.8 | 1 | 1100 | -800 | 800 | 0 | 9999 | 1 | TRUE | 0 | 0
56 | Gen_'3 ' | 6500_TRONDHEIM | TRUE | TRUE | 201.25 | 0.8 | 1 | 1100 | -800 | 800 | 0 | 9999 | 1 | TRUE | 0 | 0
57 | Gen_'4 ' | 6500_TRONDHEIM | TRUE | TRUE | 201.25 | 0.8 | 1 | 1100 | -800 | 800 | 0 | 9999 | 1 | TRUE | 0 | 0
58 | Gen_'1 ' | 6700_ROSSAGA | TRUE | TRUE | 520.25 | 0.8 | 1.02 | 1200 | -900 | 900 | 0 | 9999 | 1 | TRUE | 0 | 0
59 | Gen_'2 ' | 6700_ROSSAGA | TRUE | TRUE | 520.25 | 0.8 | 1.02 | 1200 | -900 | 900 | 0 | 9999 | 1 | TRUE | 0 | 0
60 | Gen_'3 ' | 6700_ROSSAGA | TRUE | TRUE | 520.25 | 0.8 | 1.02 | 1200 | -900 | 900 | 0 | 9999 | 1 | TRUE | 0 | 0
61 | Gen_'4 ' | 6700_ROSSAGA | TRUE | TRUE | 520.25 | 0.8 | 1.02 | 1200 | -900 | 900 | 0 | 9999 | 1 | TRUE | 0 | 0
62 | Gen_'1 ' | 7000_HELSINKI | TRUE | TRUE | 707.429 | 0.8 | 1 | 1278 | -911 | 911 | 0 | 9999 | 1 | TRUE | 0 | 0
63 | Gen_'2 ' | 7000_HELSINKI | TRUE | TRUE | 707.429 | 0.8 | 1 | 1278 | -911 | 911 | 0 | 9999 | 1 | TRUE | 0 | 0
64 | Gen_'3 ' | 7000_HELSINKI | TRUE | TRUE | 707.429 | 0.8 | 1 | 1278 | -911 | 911 | 0 | 9999 | 1 | TRUE | 0 | 0
65 | Gen_'4 ' | 7000_HELSINKI | TRUE | TRUE | 707.429 | 0.8 | 1 | 1278 | -911 | 911 | 0 | 9999 | 1 | TRUE | 0 | 0
66 | Gen_'5 ' | 7000_HELSINKI | TRUE | TRUE | 707.429 | 0.8 | 1 | 1278 | -911 | 911 | 0 | 9999 | 1 | TRUE | 0 | 0
67 | Gen_'6 ' | 7000_HELSINKI | TRUE | TRUE | 707.429 | 0.8 | 1 | 1278 | -911 | 911 | 0 | 9999 | 1 | TRUE | 0 | 0
68 | Gen_'7 ' | 7000_HELSINKI | TRUE | TRUE | 707.429 | 0.8 | 1 | 1278 | -911 | 911 | 0 | 9999 | 1 | TRUE | 0 | 0
69 | Gen_'8 ' | 7000_HELSINKI | TRUE | TRUE | 707.429 | 0.8 | 1 | 1278 | -911 | 911 | 0 | 9999 | 1 | TRUE | 0 | 0
70 | Gen_'9 ' | 7000_HELSINKI | TRUE | TRUE | 707.429 | 0.8 | 1 | 1278 | -911 | 911 | 0 | 9999 | 1 | TRUE | 0 | 0
71 | Gen_'1 ' | 7100_OULU | TRUE | TRUE | 450.047 | 0.8 | 1 | 1000 | -700 | 700 | 0 | 9999 | 1 | TRUE | 0 | 0
72 | Gen_'2 ' | 7100_OULU | TRUE | TRUE | 450.047 | 0.8 | 1 | 1000 | -700 | 700 | 0 | 9999 | 1 | TRUE | 0 | 0
73 | Gen_'3 ' | 7100_OULU | TRUE | TRUE | 450.047 | 0.8 | 1 | 1000 | -700 | 700 | 0 | 9999 | 1 | TRUE | 0 | 0
74 | Gen_'1 ' | 8500_MALMO | TRUE | TRUE | 169.333 | 0.8 | 1.02 | 1300 | -917 | 917 | 0 | 9999 | 1 | TRUE | 0 | 0
75 | Gen_'2 ' | 8500_MALMO | TRUE | TRUE | 169.333 | 0.8 | 1.02 | 1300 | -917 | 917 | 0 | 9999 | 1 | TRUE | 0 | 0
76 | Gen_'3 ' | 8500_MALMO | TRUE | TRUE | 169.333 | 0.8 | 1.02 | 1300 | -917 | 917 | 0 | 9999 | 1 | TRUE | 0 | 0
77 | Gen_'4 ' | 8500_MALMO | TRUE | TRUE | 169.333 | 0.8 | 1.02 | 1300 | -917 | 917 | 0 | 9999 | 1 | TRUE | 0 | 0
78 | Gen_'5 ' | 8500_MALMO | TRUE | TRUE | 169.333 | 0.8 | 1.02 | 1300 | -917 | 917 | 0 | 9999 | 1 | TRUE | 0 | 0
79 | Gen_'6 ' | 8500_MALMO | TRUE | TRUE | 169.333 | 0.8 | 1.02 | 1300 | -917 | 917 | 0 | 9999 | 1 | TRUE | 0 | 0

## shunt
name | bus | active | G | B | mttf | mttr

## wires
wire_name | r | x | gmr | xpos | ypos | phase

## overhead_line_types
tower_name | earth_resistivity | frequency | R1 | X1 | Gsh1 | Bsh1 | R0 | X0 | Gsh0 | Bsh0 | wire_name | xpos | ypos | phase | r | x | gmr

## underground_cable_types
name | R | X | G | B | R0 | X0 | G0 | B0

## sequence_line_types
name | R | X | G | B | R0 | X0 | G0 | B0

## transformer_types
name | HV_nominal_voltage | LV_nominal_voltage | Nominal_power | Copper_losses | Iron_losses | No_load_current | Short_circuit_voltage